## Methodology
Item | Description
Purpose | Full calculation trail for TPWODL (Odisha), FY 2023-24 (Pass 1, permitted repository only). Applicable regulation re-established: OERC (Licensees' Standards of Performance) Regulations, 2004 (S1) as amended by the 1st Amendment Regulations, 2010 (S2); no repeal, replacement or later amendment found in the repository.
Colour convention | Blue = values transcribed from source documents; black = formulas; green = links to other sheets.
Reported-performance source | OERC statement 'Performance of Electricity Distribution Companies in Odisha during the FY 2023-24 (as reported and furnished through an affidavit): Achievement on Overall Standards of Performance' (S3), single page, TPWODL column 'For the year 2023-24'. All values are annual. Values transcribed in OSoP_Reported; the TPWODL column alignment was verified against a rendered image of the page.
Restoration shares | S3 reports annual within-standard shares for urban and rural areas separately. S1 Sch. II sets one aggregate threshold over total cases. The combined FY share lies between the two area shares for any case weights. Where both are equal (fuse-off: 100.00 / 100.00) the combined share is that value without case counts. Where they differ (line breakdown 99.96 / 100.00; distribution transformer 98.70 / 85.75) the combined share is not derived because case counts are not reported. Status on the S1 basis: met under any weighting if the lower area share is at or above the threshold; not met under any weighting if the higher is below; otherwise not determinable (Restoration_Shares). Distribution transformer is not determinable (rural below, urban above 95%), so the dashboard marks it not comparable.
Ratio standards | Faulty-bill share (not more than 0.1%) and defective-meter share (not more than 5%) are single annual reported values compared directly with the S1 threshold, read as per cent per the S3 labels. The defective-meter result depends on this reading (8.36% if read as a fraction) and is flagged (Threshold_Tests). Scheduled-outage and street-light rows are not compared.
Reliability indices | S1 Sch. II 1.5 formulas (p.15): SAIFI = sum(Ai x Ni) / Nt; SAIDI = sum(Bi x Ni) / Nt; MAIFI = sum(Ci x Ni) / Nt, Ni = connected load of feeder i affected, Nt = total 11 kV connected load. S3 reports annual values 'faced by 1 KW connected load' with units (Nos.) and (Minutes). No components are reported; values are used as reported (Reliability).
Voltage cases | S3 reports HT 9 under 'No. of cases'; EHT and LT '--'. Read as a count per the label (whole number; the FY 2022-23 value 1.5 was fractional). S1 sets voltage limits but no threshold for the number of cases, so no comparison is made (Voltage_Cases).
Accidents | S3 'No. of accident cases' for FY 2022-23 and FY 2023-24. FY 2023-24 counts used; FY 2022-23 counts reconcile with the FY 2022-23 workbook (Interyear_Continuity).
Annualisation | All reported values are annual; no annualisation, summation or averaging of sub-annual values was performed. No unit conversions were required (SAIDI already in minutes).
Assumptions | None beyond the documented treatments: (i) Sch. I 1.2 time limits applied to Sch. II 1.1; (ii) 'towns and cities' treated as 'urban areas'; (iii) S3 faulty-bill parameter treated as the S1 billing-mistake parameter; (iv) faulty-bill and defective-meter values read as per cent; (v) voltage-case value read as a count.
Template | TPWODL FY 2022-23 workbooks used as the primary formatting template; all FY 2023-24 values, units, thresholds and comparison decisions re-established from the current sources.
Dashboard transfer | Dashboard_Transfer links each main-sheet value to its calculation cell and builds the annualised text with formulas; QC_Gate records the final checks.

## OSoP_Reported
Ref | Parameter (as published) | Area | Minimum target fixed by the Commission (as printed) | Target (numeric) | TPWODL FY 2023-24 (as printed) | TPWODL value (numeric) | Unit (as published) | Source
R1 | Rectification of fuse-off call within 6 hrs. of receiving the complaint in urban areas | Urban | 90 | 90 | 100.00 | 100 | % | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1
R2 | Rectification of fuse-off call within 24 hrs. of receiving the complaint in rural areas | Rural | 90 | 90 | 100.00 | 100 | % | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1
R3 | Restoration of line break-down within 12 hrs. of receiving the complaint in urban areas | Urban | 95 | 95 | 99.96 | 99.96 | % | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1
R4 | Restoration of line break-down within 24 hrs. of receiving the complaint in rural areas | Rural | 95 | 95 | 100.00 | 100 | % | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1
R5 | Replacement of Distribution Transformer within 24 hrs. of receiving the complaint in urban areas | Urban | 95 | 95 | 98.70 | 98.7 | % | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1
R6 | Replacement of Distribution Transformer within 48 hrs. of receiving the complaint in rural areas | Rural | 95 | 95 | 85.75 | 85.75 | % | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1
R7 | Completing the work within 12 hrs. of the scheduled outage before 5 PM/6 PM | All | -- |  | 100.00 | 100 | % | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1
R8 | No. of cases in which voltage at the point of commencement of supply exceeded 3% of the voltage limits: EHT | All | -- |  | -- |  | count | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1
R9 | Same: HT (S3 wording: 'No. of cases in which voltage at the point of commencement of supply exceeded 3% of the voltage limits') | EHT | (blank) |  | 9 | 9 | count | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1
R10 | Same: HT | HT | (blank) |  | -- |  | count | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1
R11 | Same: LT | LT | (blank) |  | -- |  | count | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1
R12 | Rectification of Street light fault within 6 hrs. of receiving the complaint | All | 90 | 90 | -- |  | % | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1
R13 | No. of faulty bills prepared as a percentage of total no. of bills issued | All | 0.1 | 0.1 | 0.0005 | 0.0005 | % | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1
R14 | No. of faulty/defective meters as a percentage of total no. of existing meters | All | 5 | 5 | 0.0836 | 0.0836 | % | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1
R15 | Total no. of interruption each lasting more than 5 minutes faced by 1 KW connected load (SAIFI)(Nos.) | All | (blank) |  | 428 | 428 | Nos. per 1 kW | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1
R16 | Total no. of interruption each lasting less than 5 minutes faced by 1 KW connected load (MAIFI)(Nos.) | All | (blank) |  | 43 | 43 | Nos. per 1 kW | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1
R17 | Total duration of interruption in minutes each 1 KW connected load (SAIDI)(Minutes) | All | (blank) |  | 18312 | 18312 | Minutes per 1 kW | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1

## Restoration_Shares
Parameter | Urban share (%) | Rural share (%) | Lower area share (%) | Higher area share (%) | Combined FY share (%) | Regulatory threshold (%) (S1) | Commission target shown in S3 (%) | Threshold check (S1 = S3) | Comparison possible? (dashboard decision) | Aggregate test on S1 basis | Area-level test (S3 presentation) | Source / note | S1-basis status (before dashboard decision)
Normal fuse-off call rectification | 100 | 100 | 100 | 100 | 100 | 90 | 90 | OK | Yes | Yes | Both areas at or above target | S1 Sch. II 1.1 (p.14); time limits S1 Sch. I 1.2 (p.7); values OSoP_Reported R1–R2 | Met under any weighting
Line breakdown restoration | 99.96 | 100 | 99.96 | 100 | Not derivable without case counts | 95 | 95 | OK | No | N/A | Both areas at or above target | S1 Sch. II 1.2 (p.14); values OSoP_Reported R3-R4. Comparison not possible: S3 time from receipt of complaint, S1 from occurrence. Urban 99.96 / rural 100.00: combined share not derivable without case counts | Met under any weighting
Distribution transformer failure restoration | 98.7 | 85.75 | 85.75 | 98.7 | Not derivable without case counts | 95 | 95 | OK | No | N/A | At least one area below target | S1 Sch. II 1.3 (p.14); time limits S1 Sch. I 1.4 (p.7); values OSoP_Reported R5-R6. Urban 98.70 above and rural 85.75 below the threshold: aggregate result not determinable without case counts, so comparison is marked not possible | Not determinable without case counts

## Threshold_Tests
Parameter | Reported value (%) | Regulatory threshold (%) (S1) | Direction | Comparison possible? (dashboard decision) | Test result (original basis) | Margin to threshold (pp) | Source / note
Scheduled outage share | 100 | 90 | At least | No | N/A | 10 | S1 Sch. II 1.4 (p.14). Comparison not possible: standard also requires advance notice and a daily duration cap; reported item defined only as completion within 12 hours before 5 PM/6 PM
Street-light fault rectification share | No value reported | 90 | At least | No | N/A | n/a | S1 Sch. II 1.8 (p.16). No value reported for FY 2023-24
Faulty-bill share | 0.0005 | 0.1 | Not more than | Yes | Yes | 0.0995 | S1 Sch. II 1.9 (p.16); reported 0.0005 read as per cent; result unchanged if read as a fraction (0.05%)
Defective-meter share | 0.0836 | 5 | Not more than | Yes | Yes | 4.9164 | S1 Sch. II 1.10 (p.16); reported 0.0836 read as per cent; if read as a fraction (8.36%) the ceiling of 5% would be exceeded (see Data_Quality_Flags)

## Reliability
Index | Reported FY value | Unit (dashboard) | Unit evidence | Formula (S1 Sch. II 1.5, p.15) | Note
SAIDI | 18312 | Minutes per kW of connected load | S3 '(Minutes)', 'each 1 KW connected load' | Σ(Bi×Ni) ÷ Nt | Annual value; no components reported
SAIFI | 428 | Interruptions per kW of connected load | S3 '(Nos.)', 'faced by 1 KW connected load'; S1 formula (count × kW ÷ kW) | Σ(Ai×Ni) ÷ Nt | Annual value; no components reported
MAIFI | 43 | Momentary interruptions per kW of connected load | S3 '(Nos.)', 'faced by 1 KW connected load'; S1 formula | Σ(Ci×Ni) ÷ Nt | Annual value; no components reported
SAIDI in hours (information) | 305.2 | Hours per kW of connected load | Conversion ÷ 60 | Not applicable | Not used on the dashboard
Plausibility: SAIDI ÷ SAIFI | 42.785 | Minutes per interruption | Derived | Not applicable | Plausibility check only; CAIDI is not specified in S1 or reported in S3 and is not a dashboard indicator
Plausibility: MAIFI ÷ SAIFI | 0.10047 | Ratio | Derived | Not applicable | Plausibility check only

## Voltage_Cases
Voltage level | As printed | Numeric | Note
EHT | -- |  | No value reported
HT | 9 | 9 | Reported; read as a count of cases per the label (whole number)
LT | -- |  | No value reported

## Accidents
Category | FY 2022-23 (as printed) | FY 2022-23 | FY 2023-24 (as printed) | FY 2023-24 | Change (FY 2023-24 - FY 2022-23) | Source
Fatal Human | 02 | 2 | 46 | 46 | 44 | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1, accident table, TPWODL columns 22-23 / 23-24
Non-fatal Human | 24 | 24 | 44 | 44 | 20 | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1, accident table, TPWODL columns 22-23 / 23-24
Fatal Animal | 24 | 24 | 46 | 46 | 22 | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1, accident table, TPWODL columns 22-23 / 23-24
Non-fatal Animal | 00 | 0 | 00 | 0 | 0 | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1, accident table, TPWODL columns 22-23 / 23-24
Total (all categories) |  | 50 |  | 136 | 86 | Computed

## Dashboard_Transfer
Main-sheet indicator | FY value (formula) | Format | Dashboard text (Annualised / standardised reported data)
Normal fuse-off call rectification — share resolved within standard | 100 | 0.0% | FY within-standard share: 100.0%.
Line breakdown restoration — share resolved within standard | n/a | n/a | Not annualised: case counts required to combine the urban and rural shares are not reported.
Distribution transformer failure restoration — share resolved within standard | n/a | n/a | Not annualised: case counts required to combine the urban and rural shares are not reported.
Scheduled outage restoration — share resolved within standard | 100 | 0.0% | FY within-standard share: 100.0%.
Street-light fault rectification — share resolved within standard | n/a | n/a | Not annualised: no reported value.
Billing mistakes — faulty bills as share of bills issued | 0.0005 | 0.0000% | FY faulty-bill share: 0.0005%.
Defective meters — share of meters in service | 0.0836 | 0.0000% | FY defective-meter share: 0.0836%.
System Average Interruption Duration Index (SAIDI) | 18312 | #,##0 | FY SAIDI: 18,312 minutes per kW of connected load.
System Average Interruption Frequency Index (SAIFI) | 428 | #,##0 | FY SAIFI: 428 interruptions per kW of connected load.
Momentary Average Interruption Frequency Index (MAIFI) | 43 | #,##0 | FY MAIFI: 43 momentary interruptions per kW of connected load.
Supply frequency outside ±3% of 50 Hz — number of hourly measurements | n/a | n/a | Not annualised: no reported value.
Supply voltage at point of supply outside limits — number of cases (EHT / HT / LT) | 9 | 0 | FY HT cases: 9.
Fatal electrical accidents — humans | 46 | 0 | FY fatal human accidents: 46.
Non-fatal electrical accidents — humans | 44 | 0 | FY non-fatal human accidents: 44.
Fatal electrical accidents — animals | 46 | 0 | FY fatal animal accidents: 46.
Non-fatal electrical accidents — animals | 0 | 0 | FY non-fatal animal accidents: 0.

## Interyear_Continuity
Item | FY 2022-23 value in the FY 2022-23 workbook | FY 2022-23 value shown in the FY 2023-24 statement | Difference | Status | FY 2022-23 source | FY 2023-24 source
Fatal human accidents | 2 | 2 | 0 | OK | TPWODL FY 2022-23 Calculations > Accidents (S3 FY 2022-23 statement, p.1) | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1
Non-fatal human accidents | 24 | 24 | 0 | OK | TPWODL FY 2022-23 Calculations > Accidents (S3 FY 2022-23 statement, p.1) | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1
Fatal animal accidents | 24 | 24 | 0 | OK | TPWODL FY 2022-23 Calculations > Accidents (S3 FY 2022-23 statement, p.1) | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1
Non-fatal animal accidents | 0 | 0 | 0 | OK | TPWODL FY 2022-23 Calculations > Accidents (S3 FY 2022-23 statement, p.1) | S3, OERC Achievement on Overall Standards of Performance FY 2023-24, p.1

## PriorFY_Row_Check
Check | Result | Detail
Row set vs FY 2022-23 main sheet | Pass | 16 rows (FY 2022-23: 16); 16 of 16 indicator names identical in the same order; same parameters in the Commission's statement.
Row-by-row field comparison | Pass (genuine differences) | Fields changed per row (excluding financial year): Normal fuse-off call rectification: no change other than financial year; Line breakdown restoration: Reported data, Annualised / standardised reported data, Documentation of standardisation / transformation; Distribution transformer failure restoration: Reported data, Comparison possible?, Standard met?, If comparison is not possible, why?, Interpretation, Documentation of standardisation / transformation; Scheduled outage restoration: no change other than financial year; Street-light fault rectification: Reported data, If comparison is not possible, why?; Billing mistakes: Reported data, Annualised / standardised reported data; Defective meters: Reported data, Annualised / standardised reported data; System Average Interruption Duration Index (SAIDI): Reported data, Annualised / standardised reported data, If comparison is not possible, why?; System Average Interruption Frequency Index (SAIFI): Reported data, Annualised / standardised reported data, If comparison is not possible, why?; Momentary Average Interruption Frequency Index (MAIFI): Reported data, Annualised / standardised reported data, If comparison is not possible, why?; Supply frequency outside ±3% of 50 Hz: Reported data, If comparison is not possible, why?; Supply voltage at point of supply outside limits: Reported data, Annualised / standardised reported data, If comparison is not possible, why?, Interpretation; Fatal electrical accidents: Reported data, Annualised / standardised reported data; Non-fatal electrical accidents: Reported data, Annualised / standardised reported data; Fatal electrical accidents: Reported data, Annualised / standardised reported data; Non-fatal electrical accidents: no change other than financial year
Rows unchanged apart from financial year | Pass | Normal fuse-off call rectification, Scheduled outage restoration, Non-fatal electrical accidents
Comparison / compliance logic | Pass (genuine differences) | Distribution transformer moves from Yes/Yes to No/N/A: urban 98.70% is above and rural 85.75% below the 95% aggregate threshold, and case counts are not reported. Line breakdown stays No/N/A with differing area shares. 3 rows Yes/Yes (fuse-off, faulty bills, defective meters); 13 rows No/N/A.
Standards | Pass | Standard column identical to FY 2022-23 because S1 (as amended by S2) is unchanged; re-checked against S1 Sch. I and II.
Supporting-sheet and calculations structure | Pass | Same sheet set as FY 2022-23; Restoration_Shares gains an S1-basis status column.
Substantive evidence re-established | Pass | All values, page references, flags and review items re-extracted from the FY 2023-24 statement and S1/S2; none copied from earlier years.

## QC_Gate
Check | Result | Evidence
Full permitted repository searched | Pass | Repository: S1, S2, S3 (FY 2023-24 statement), the FY 2022-23 and FY 2021-22 statements, the context document, the previous TPWODL workbooks and the UGVCL reference workbooks. The connected Google Drive was searched again (TPWODL, Overall Standards of Performance, OERC); no relevant documents found.
Regulatory and reported-performance sources reviewed | Pass | Regulatory: S1 and S2 re-read for applicability to FY 2023-24. Reported: S3 (single page, text and rendered image).
Applicable regulation re-established | Pass | S1 as amended by S2 in force throughout FY 2023-24; no repeal or replacement found (recorded in Source_Gaps).
Amendments checked | Pass (gap recorded) | S2 does not alter Schedule II standards or formulas. No later amendment found; recorded in Source_Gaps.
Definitions, units, formulas, reporting basis re-verified | Pass | Thresholds from S1 Sch. II; reliability formulas S1 p.15 (connected-load weighting); units from S3 labels and S1 formulas; reporting basis annual (S3).
Unit check: every quantitative indicator | Pass | Shares %; SAIDI minutes per kW; SAIFI interruptions per kW; MAIFI momentary interruptions per kW; voltage cases count; accidents count. Meter-share unit reading flagged.
Annualisation-method check | Pass | All values annual; no summing, averaging, multiplication or extrapolation. Combined urban/rural shares derived only where both area shares are equal.
Detailed-figures check (Reported data and Annualised fields) | Pass | Automated scan of 16 rows: no counts, numerators, denominators, balances, prior-year values or inputs.
Comparison possible? / Standard met? logic | Pass | 16 of 16 rows consistent: 13 rows No / N/A; 3 rows Yes / Yes, each assessed on the original S1 basis.
Standards not transformed | Pass | Standards stated as aggregate shares or limits exactly as in S1.
Main sheet columns and public-facing language | Pass | Exact 13 prescribed columns; internal-process phrase scan clean.
Dashboard transfer reconciliation | Pass | Annualised text in Dashboard_Transfer (formula-built or fixed) matches the main sheet for all 16 rows (automated check after recalculation).
Row-by-row consistency with FY 2022-23 | Pass | See PriorFY_Row_Check.
Reconciliations and flags | Pass (flags documented) | Threshold check S1 = S3 targets: OK. Accident continuity with FY 2022-23 workbook: OK. Data flags recorded in Data_Quality_Flags.