## Main
State | DISCOM | Financial year | Indicator category | Indicator | Standard | Reported data | Annualised / standardised reported data | Comparison possible? | Standard met? | If comparison is not possible, why? | Interpretation | Documentation of standardisation / transformation
Odisha | TPWODL | FY 2024-25 | Quality of Service | Normal fuse-off call rectification — share resolved within standard | At least 90% of fuse-off calls rectified within 6 hours (Urban) / 24 hours (Rural) of complaint | Within-standard share (FY, annual reporting): Urban 100.00%; Rural 100.00%. | FY within-standard share: 100.0%. | Yes | Yes | Not applicable. | Performance met the applicable regulatory standard. | FY share for urban and rural areas combined derived from the two reported area shares, which are both 100.00%, so the result does not depend on the unreported case counts; reported on an annual basis, so no annualisation was required.
Odisha | TPWODL | FY 2024-25 | Quality of Service | Line breakdown restoration — share resolved within standard | At least 95% of line breakdowns restored within 12 hours (Urban) / 24 hours (Rural) of occurrence of the breakdown | Within-standard share (FY, annual reporting; time measured from receipt of complaint): Urban 100.00%; Rural 100.00%. | FY within-standard share (time measured from receipt of complaint): 100.0%. | No | N/A | The standard measures restoration time from the occurrence of the breakdown, while the reported share measures it from receipt of the complaint, which may be later; the reported share therefore does not measure performance against the regulatory time limit. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY share for urban and rural areas combined derived from the two reported area shares, which are both 100.00%, so the result does not depend on the unreported case counts; reported on an annual basis, so no annualisation was required.
Odisha | TPWODL | FY 2024-25 | Quality of Service | Distribution transformer failure restoration — share resolved within standard | At least 95% of failed distribution transformers replaced within 24 hours (Urban) / 48 hours (Rural) of complaint | Within-standard share (FY, annual reporting): Urban 96.39%; Rural 85.01%. | Not annualised: case counts required to combine the urban and rural shares are not reported. | No | N/A | The standard applies to the aggregate share across all failed distribution transformers, while reported data give only separate urban and rural shares; the rural share is below the 95% threshold and the urban share is above it, so whether the aggregate share meets the threshold cannot be determined without case counts, which are not reported. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | Combined urban and rural share not derived because case counts are not reported; reported on an annual basis, so no annualisation was required.
Odisha | TPWODL | FY 2024-25 | Quality of Service | Scheduled outage restoration — share resolved within standard | At least 90% of scheduled outages notified in advance (at least 24 hours), not exceeding 12 hours a day, and with supply restored by 6 p.m. (summer) / 5 p.m. (winter) | Within-standard share (FY, annual reporting): 100.00%. | FY within-standard share: 100.0%. | No | N/A | The standard requires advance notice (at least 24 hours), a duration of not more than 12 hours a day and restoration by 6 p.m. (summer) / 5 p.m. (winter), each in at least 90% of cases, while the reported share is defined only as work completed within 12 hours of the scheduled outage before 5 p.m. / 6 p.m.; it does not cover advance notice or state the season-specific restoration time. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | None; reported on an annual basis, so no annualisation was required.
Odisha | TPWODL | FY 2024-25 | Quality of Service | Street-light fault rectification — share resolved within standard | At least 90% of street-light faults rectified within 6 hours of detection or complaint, whichever is earlier | No value reported for FY 2024-25. | Not annualised: no reported value. | No | N/A | No reported value is available for FY 2024-25. | Direct comparison is not possible because no reported value is available. | Not annualised because no reported value is available.
Odisha | TPWODL | FY 2024-25 | Quality of Service | Billing mistakes — faulty bills as share of bills issued | Bills requiring rectification following complaints not more than 0.1% of bills issued | Faulty bills as a share of bills issued (FY, annual reporting): 0.00%. | FY faulty-bill share: 0.00%. | Yes | Yes | Not applicable. | Performance met the applicable regulatory standard. | None
Odisha | TPWODL | FY 2024-25 | Quality of Service | Defective meters — share of meters in service | Defective meters not more than 5% of meters in service | Defective meters as a share of meters in service (FY, annual reporting): 0.05%. | FY defective-meter share: 0.05%. | Yes | Yes | Not applicable. | Performance met the applicable regulatory standard. | None
Odisha | TPWODL | FY 2024-25 | Quality & Reliability of Supply | System Average Interruption Duration Index (SAIDI) | No quantitative benchmark specified (target levels may be notified by the Commission annually under the regulation) | Annual SAIDI (minutes per kW of connected load): 20,684. | FY SAIDI: 20,684 minutes per kW of connected load. | No | N/A | No quantitative reliability target applicable to FY 2024-25 is available; the regulation provides for the Commission to notify target levels annually. In addition, the regulation requires the indices to be computed monthly and reported separately for urban and rural feeders, while only a single annual value is reported, without monthly, urban/rural or agricultural-feeder disaggregation. | No quantitative regulatory benchmark is specified for direct comparison. | None
Odisha | TPWODL | FY 2024-25 | Quality & Reliability of Supply | System Average Interruption Frequency Index (SAIFI) | No quantitative benchmark specified (target levels may be notified by the Commission annually under the regulation) | Annual SAIFI (interruptions per kW of connected load): 424. | FY SAIFI: 424 interruptions per kW of connected load. | No | N/A | No quantitative reliability target applicable to FY 2024-25 is available; the regulation provides for the Commission to notify target levels annually. In addition, the regulation requires the indices to be computed monthly and reported separately for urban and rural feeders, while only a single annual value is reported, without monthly, urban/rural or agricultural-feeder disaggregation. | No quantitative regulatory benchmark is specified for direct comparison. | None
Odisha | TPWODL | FY 2024-25 | Quality & Reliability of Supply | Momentary Average Interruption Frequency Index (MAIFI) | No quantitative benchmark specified (target levels may be notified by the Commission annually under the regulation) | Annual MAIFI (momentary interruptions per kW of connected load): 62. | FY MAIFI: 62 momentary interruptions per kW of connected load. | No | N/A | No quantitative reliability target applicable to FY 2024-25 is available; the regulation provides for the Commission to notify target levels annually. In addition, the regulation requires the indices to be computed monthly and reported separately for urban and rural feeders, while only a single annual value is reported, without monthly, urban/rural or agricultural-feeder disaggregation. | No quantitative regulatory benchmark is specified for direct comparison. | None
Odisha | TPWODL | FY 2024-25 | Quality & Reliability of Supply | Supply frequency outside ±3% of 50 Hz — number of hourly measurements | Licensee to endeavour to maintain supply frequency within ±3% of 50 Hz and report the number of hourly measurements outside this range; no numerical target specified | No value reported for FY 2024-25. | Not annualised: no reported value. | No | N/A | The regulation does not specify a quantitative benchmark for the number of supply-frequency excursions, and no reported value is available for FY 2024-25. | No quantitative regulatory benchmark is specified for direct comparison. | Not annualised because no reported value is available.
Odisha | TPWODL | FY 2024-25 | Quality & Reliability of Supply | Supply voltage at point of supply outside limits — number of cases (EHT / HT / LT) | +6% / −6% (LV); +6% / −9% (HV); +10% / −12.5% (EHV) of declared voltage | Number of cases (FY, annual reporting): HT 0.08; LT 0; no value reported for EHT. | FY HT value: 0.08; LT value: 0 (unit not established). | No | N/A | The reported HT value (0.08) is fractional, so it cannot be confirmed as a count of cases, and no unit could be established from the regulation; in addition, the standard applies to the voltage at each consumer's point of supply, and no aggregate threshold for the number of cases outside the limits is specified. | Direct comparison is not possible because the unit of the reported value could not be established and no aggregate benchmark is specified. | None; reported on an annual basis, so no annualisation was required.
Odisha | TPWODL | FY 2024-25 | Safety | Fatal electrical accidents — humans | No quantitative benchmark specified | Number of accidents (FY): 8. | FY fatal human accidents: 8. | No | N/A | The applicable regulation does not specify a quantitative benchmark for the number of electrical accidents; it identifies the change in the number of accidents over time as an indicator of performance, without a target. | No quantitative regulatory benchmark is specified for direct comparison. | None
Odisha | TPWODL | FY 2024-25 | Safety | Non-fatal electrical accidents — humans | No quantitative benchmark specified | Number of accidents (FY): 12. | FY non-fatal human accidents: 12. | No | N/A | The applicable regulation does not specify a quantitative benchmark for the number of electrical accidents; it identifies the change in the number of accidents over time as an indicator of performance, without a target. | No quantitative regulatory benchmark is specified for direct comparison. | None
Odisha | TPWODL | FY 2024-25 | Safety | Fatal electrical accidents — animals | No quantitative benchmark specified | Number of accidents (FY): 28. | FY fatal animal accidents: 28. | No | N/A | The applicable regulation does not specify a quantitative benchmark for the number of electrical accidents; it identifies the change in the number of accidents over time as an indicator of performance, without a target. | No quantitative regulatory benchmark is specified for direct comparison. | None
Odisha | TPWODL | FY 2024-25 | Safety | Non-fatal electrical accidents — animals | No quantitative benchmark specified | Number of accidents (FY): 0. | FY non-fatal animal accidents: 0. | No | N/A | The applicable regulation does not specify a quantitative benchmark for the number of electrical accidents; it identifies the change in the number of accidents over time as an indicator of performance, without a target. | No quantitative regulatory benchmark is specified for direct comparison. | None

## Source_Documentation
ID | Source type | Source file name | Document title | Issuing authority | Publication / FY | Page(s) | Section / table / annexure | Google Drive link | Source note
S1 | Regulatory | Odisha_Principal_Regulation_2004.pdf | Orissa Electricity Regulatory Commission (Licensees' Standards of Performance) Regulations, 2004, Notification No. OERC-Engg-94/2003, dated 21 May 2004 | Orissa Electricity Regulatory Commission | Orissa Gazette Extraordinary No. 711, 28 May 2004; in force from publication (Reg. 1(4)); applicable throughout FY 2024-25 as amended by S2 | p.2 (Regs. 1-2); p.3 (Regs. 2-4); pp.4-5 (Regs. 5-6); pp.5-6 (Regs. 8-12); pp.7-13 (Schedule I); pp.14-16 (Schedule II); pp.17-19 (Schedule III) | Regs. 1-12; Schedule I (Guaranteed Standards); Schedule II (Overall Standards, incl. 1.5 reliability-index formulas, p.15); Schedule III (compensation) | Not available: file supplied in the permitted repository without a Google Drive URL | Applicable regulation for FY 2024-25. Source of all overall standards, thresholds, reliability-index formulas (connected-load weighted) and the accident provision. No repeal or replacement located in the permitted repository. Re-checked for FY 2024-25: no repeal, replacement or later amendment located in the permitted repository.
S2 | Regulatory | Odisha_1st_Amendment_2010.pdf | Orissa Electricity Regulatory Commission (Licensee's Standard of Performance) (1st Amendment) Regulations, 2010, Notification No. OERC-Engg.-94/2003(Vol.-III)/5584, dated 16 December 2010 | Orissa Electricity Regulatory Commission | Notified 16 December 2010; in force from publication in the Official Gazette (gazette date not stated in the file); applicable throughout FY 2024-25 | pp.1-3 | Clauses 1-6: Reg. 3(2)-3(8) (call centres; definition of Urban Areas); new Reg. 8 (third-party audit); renumbering of Regs. 8-12 as 9-13; amended Reg. 9(1) (force majeure); new Schedule I clause 3.8 (temporary supply) | Not available: file supplied in the permitted repository without a Google Drive URL | Reviewed. Does not amend the Schedule II overall standards or the reliability-index formulas. Urban Areas definition (p.1) used to confirm that 'towns and cities' (S1) and 'urban areas' (S3) refer to the same area classification. Re-checked for FY 2024-25: no repeal, replacement or later amendment located in the permitted repository.
S3 | Reported performance | Overall_Standards_of_Performance_3.pdf | Performance of Electricity Distribution Companies in Odisha during the FY 2024-25 (as reported and furnished through an affidavit): Achievement on Overall Standards of Performance | Odisha Electricity Regulatory Commission (data furnished by the distribution licensees through affidavit) | FY 2024-25 (annual values; accident counts also shown for FY 2023-24); statement reference OERC.-11011(11)/1/2026-ENGG DIV-OERC I/21639/2026; no issue date printed | p.1 (single page) | Single table; TPWODL column ('For the year 2024-25'); column 'Minimum % target fixed by the Commission'; accident table (23-24 / 24-25); Notes 1-2 | Not available: file supplied in the permitted repository without a Google Drive URL | Reported annual performance for TPWODL. SAIFI/MAIFI unit '(Nos.)' and SAIDI unit '(Minutes)' stated in the parameter labels, each 'faced by 1 KW connected load'; weighting confirmed against S1 Schedule II formulas. Share values are printed with percent signs in this statement. TPWODL column alignment (including the EHT / HT / LT voltage block) verified on a rendered image of the page. The statements for FY 2023-24, FY 2022-23 and FY 2021-22 are separate documents with the same layout; they are used here only for the continuity check in the calculations workbook.

## Regulatory_Standards
Service / indicator | Area | Standard (original regulatory basis) | Source | Standard basis | Reporting format
Information on likely restoration time | All | Within 4 hours of complaint, on enquiry by the consumer | S1 Sch. I 1.1, p.7 | Event-level time standard | Not reported in S3
Normal fuse-off (supply restoration) | Urban / Rural | 6 hours (towns and cities); 24 hours (rural areas) from receipt of complaint (HG or LT fuses at the distribution transformer or consumer premises) | S1 Sch. I 1.2, p.7 | Event-level time standard | S3 p.1, rows 'Rectification of fuse-off call within 6 hrs. / 24 hrs.'
Normal fuse-off calls (overall) | All (total calls received) | Percentage of fuse-off calls rectified within the Schedule I time limits to total calls received not less than 90% | S1 Sch. II 1.1, p.14 (cross-refers to Sch. I sub-para 1.1; see Data_Quality_Flags) | Aggregate share threshold | S3 p.1, Urban and Rural rows; Commission's minimum target 90 shown for each area
Line breakdowns (supply restoration) | Urban / Rural | 12 hours (towns and cities); 24 hours (rural areas) from occurrence of breakdown; major breakdowns (heavy rain, lightning, whirlwind, needing conductor/structure replacement) 24 hours / 48 hours | S1 Sch. I 1.3, p.7 | Event-level time standard | S3 p.1 (measured 'of receiving the complaint')
Line breakdowns (overall) | Urban / Rural | Restoration within 12 hours (towns and cities) / 24 hours (rural areas) of occurrence of breakdown in at least 95% of cases | S1 Sch. II 1.2, p.14 | Aggregate share threshold | S3 p.1, Urban and Rural rows; minimum target 95
Distribution transformer failure (supply restoration) | Urban / Rural | Replacement within 24 hours (towns and cities); 48 hours (rural areas) of receiving the complaint | S1 Sch. I 1.4, p.7 | Event-level time standard | S3 p.1
Distribution transformer failures (overall) | All (total DTs failed) | Percentage of DTs replaced within the Schedule I time limits to total DTs failed not less than 95% | S1 Sch. II 1.3, p.14 | Aggregate share threshold | S3 p.1, Urban and Rural rows; minimum target 95
Scheduled outages | All | Notified at least 24 hours in advance; not more than 12 hours in a day; supply restored by 6 p.m. (summer) / 5 p.m. (winter) | S1 Sch. I 1.5, p.7 | Event-level | See next row
Scheduled outages (overall) | All | Both standards (duration and restoration time) achieved in at least 90% of cases | S1 Sch. II 1.4, p.14 | Aggregate share threshold | S3 p.1, row 'Completing the work within 12 hrs. of the scheduled outage before 5 PM/6 PM'; TPWODL 100.00; minimum target 90
Voltage variations | LV / HV / EHV | +6% / −6% (LV); +6% / −9% (HV); +10% / −12.5% (EHV) of declared voltage, at the point of commencement of supply; complaint: improve within 15 days (no network expansion), resolve within 120 days (up to 11 kV) / 180 days (up to 33 kV); intimate within 7 days if due to transmission | S1 Sch. I 2.1, p.8 | Point-of-supply limit; event-level complaint times | S3 p.1, row 'No. of cases in which voltage at the point of commencement of supply exceeded 3% of the voltage limits' (EHT/HT/LT); TPWODL HT 0.08, LT 0, EHT '-'
Harmonics | ≥132 kV / 33 kV / 11 kV consumers | THDv limited to 3% (132 kV and above), 8% (33 kV), 8% (11 kV) per Orissa Grid Code; Stage 1 effective on Commission order; Stages 2-3 dates to be set | S1 Sch. I 2.2, pp.8-9 | Point-of-supply limit (staged) | Not reported in S3
Meter complaints | All | Inspect within 7 working days; replace defective licensee meter within 30 days; burnt meter (not consumer-caused) within 30 working days; consumer-caused: notice within 7 days, replace within 15 days of payment | S1 Sch. I 2.3, p.9 | Event-level time standard | Not reported in S3
New connections / additional load | LT / HT / EHT | Notice within 3 days and estimate within one week (LT); feasibility 21/30 working days and estimate 60 working days (HT/EHT); supply within one month (no extension), 30/60/90 days (LT/11 kV/33 kV extension); temporary supply sanction within 3 days (Urban) / 7 days (Rural) | S1 Sch. I 3.1-3.7, pp.9-12; S2 cl. 6 (Sch. I 3.8), p.3 | Event-level time standard | Not reported in S3
Transfer of ownership and conversion of services | All | 15 days (title transfer, change of category); 30 / 60 / 90 days (LT 1-ph↔3-ph / LT↔11 kV / LT↔33 kV conversion) | S1 Sch. I 4, p.12 | Event-level time standard | Not reported in S3
Bill complaints and reconnection | All | Bill complaints resolved within 30 days; reconnection within 4 working hours of proof of payment | S1 Sch. I 5.1-5.2, p.13 | Event-level time standard | Not reported in S3
SAIFI / SAIDI / MAIFI | Licensee-wide 11 kV feeders excl. predominantly agricultural; agricultural feeders separately; urban / rural separately; monthly | Indices per IEEE 1366 (1998) computed with connected-load weighting: SAIFI = Σ(Ai×Ni) ÷ Nt; SAIDI = Σ(Bi×Ni) ÷ Nt; MAIFI = Σ(Ci×Ni) ÷ Nt (sustained > 5 minutes; momentary ≤ 5 minutes). No numeric target; the Commission may notify target levels annually | S1 Sch. II 1.5, pp.14-15 | None (target not available) | S3 p.1, annual values for TPWODL; target column blank
Supply frequency | All | Endeavour to maintain within ±3% of 50 Hz; hourly measurement; report number of events outside limits | S1 Sch. II 1.6, p.16 | No quantitative benchmark (reporting obligation) | S3 p.1; TPWODL '--'
Voltage unbalance | All | Not to exceed 3% at the point of commencement of supply; computation method to be specified separately | S1 Sch. II 1.7, p.16 | Point-of-supply limit | Not reported in S3
Street-light faults | All | Rectify line faults and restore street lights within 6 hours of detection or receipt of complaint, whichever is earlier, in at least 90% of cases | S1 Sch. II 1.8, p.16 | Aggregate share threshold | S3 p.1 (measured 'of receiving the complaint'); minimum target 90; TPWODL '--'
Billing mistakes | All | Percentage of bills requiring rectification following complaints to total bills issued not greater than 0.1% | S1 Sch. II 1.9, p.16 | Aggregate share ceiling | S3 p.1, row 'No. of faulty bills prepared as a percentage of total no. of bills issued'; minimum target column 0.1
Faulty meters | All | Percentage of defective meters to total meters in service not greater than 5% | S1 Sch. II 1.10, p.16 | Aggregate share ceiling | S3 p.1, row 'No. of faulty/defective meters as a percentage of total no. of existing meters'; minimum target column 5
Electrical accidents | All | Licensee to endeavour to minimise electrical accidents; increase or decrease over time is an indicator of performance. No numeric benchmark | S1 Sch. II 1.11, p.16 | No quantitative benchmark | S3 p.1, accident table (fatal / non-fatal, human / animal; 23-24 and 24-25)
Compensation to consumers | Urban / other areas | Schedule of compensation (Rs. 50 to Rs. 1,000 per case or per day of default; automatic or to be claimed) for failure to meet Guaranteed Standards | S1 Reg. 5; Sch. III, pp.17-19 | Compensation schedule | Not reported in S3
Reporting obligations | All | Guaranteed Standards: monthly reports within 15 days and annual report within 30 days of year-end. Overall Standards: quarterly reports within 15 days and annual report within 30 days of year-end | S1 Reg. 6(1)-6(4), pp.4-5 | Reporting basis | Only the Commission's consolidated annual statement (S3) is available
Force majeure exemption | All | Standards suspended during force majeure, including outages due to generation or transmission failure and outages initiated by NLDC / RLDC / SLDC | S1 Reg. 8(1) as renumbered and amended as Reg. 9(1) by S2 cl. 4-5, p.3 | Exemption | Application to reported values not stated in S3

## Definitions_Units
Indicator | Definition / formula | Dashboard unit | Reporting basis | Evidence | Note
Within-standard share (fuse-off, line breakdown, distribution transformer, scheduled outage, street light) | Cases rectified / restored / replaced within the Schedule I time limit ÷ total cases (calls received; DTs failed) × 100 | Percentage (%) | Annual (FY 2024-25), urban and rural reported separately for the first three parameters | S1 Sch. II 1.1-1.4, 1.8, p.14, p.16; S3 p.1 ('Achievement in %') | Underlying case counts are not reported. Line-breakdown rows in S3 measure time from receipt of complaint (S1: occurrence of breakdown). Scheduled-outage row in S3 is worded 'completing the work within 12 hrs. of the scheduled outage before 5 PM/6 PM' (S1 also requires advance notice and a daily duration cap). Street-light share not reported for FY 2024-25. Where urban and rural shares differ the S1 aggregate share cannot be derived.
Faulty-bill share | Bills requiring rectification following complaints ÷ total bills issued × 100 (S1); 'faulty bills prepared as a percentage of total no. of bills issued' (S3) | Percentage (%) | Annual | S1 Sch. II 1.9, p.16; S3 p.1 | Reported to two decimal places (0.00%) with a percent sign in S3. Wording differs between S1 and S3; see Data_Quality_Flags.
Defective-meter share | Defective meters ÷ total meters in service × 100 | Percentage (%) | Annual (point in the year not stated) | S1 Sch. II 1.10, p.16; S3 p.1 | Reported to two decimal places (0.05%) with a percent sign in S3, which fixes the unit as per cent for FY 2024-25 (earlier statements printed the values without percent signs); see Data_Quality_Flags.
SAIDI | Σ(Bi×Ni) ÷ Nt; Bi = total duration of sustained interruptions on feeder i in the month; Ni = connected load of feeder i affected; Nt = total 11 kV connected load | Minutes per kW of connected load | Annual value | S1 Sch. II 1.5, p.15 (formula; duration unit not stated); S3 p.1 ('Total duration of interruption in minutes each 1 KW connected load (SAIDI)(Minutes)') | Connected-load weighted, not consumer weighted; not directly comparable with consumer-weighted indices of other states.
SAIFI | Σ(Ai×Ni) ÷ Nt; Ai = number of sustained interruptions (each longer than 5 minutes) on feeder i in the month | Interruptions per kW of connected load | Annual value | S1 Sch. II 1.5, p.15; S3 p.1 ('Total no. of interruption each lasting more than 5 minutes faced by 1 KW connected load (SAIFI)(Nos.)') | Unit derived from formula: (count × kW) ÷ kW = count per unit of connected load; S3 states '(Nos.)' per 1 kW.
MAIFI | Σ(Ci×Ni) ÷ Nt; Ci = number of momentary interruptions (each less than or equal to 5 minutes) on feeder i in the month | Momentary interruptions per kW of connected load | Annual value | S1 Sch. II 1.5, p.15; S3 p.1 ('... each lasting less than 5 minutes faced by 1 KW connected load (MAIFI)(Nos.)') | S1 momentary threshold '≤ 5 minutes'; S3 label 'less than 5 minutes'.
Supply-frequency excursions | Number of hourly measurements with supply frequency outside ±3% of 50 Hz | Number of hourly measurements (count) | Not reported | S1 Sch. II 1.6, p.16; S3 p.1 | No value reported.
Voltage cases outside limits | Number of cases in which voltage at the point of commencement of supply exceeded the limits (S3 wording: 'exceeded 3% of the voltage limits'; FY 2021-22 wording also cited 'I.E. Rules, 1956') | Number of cases (unit not established) | Annual; HT and LT values (EHT not reported) | S1 Sch. I 2.1, p.8; S3 p.1 | Fractional HT value in FY 2024-25 (0.08); LT 0. Earlier values: FY 2023-24 whole number 9; FY 2022-23 fractional 1.5. Label in S3 is 'No. of cases'; S1, S2 and S3 give no further reporting instruction, so the unit of a fractional value cannot be established. S3 wording does not correspond to the S1 voltage limits.
Electrical accidents (fatal / non-fatal; human / animal) | Number of accident cases in the year | Number of accidents (count) | Annual | S3 p.1 ('No. of accident cases'); S1 Sch. II 1.11, p.16 | Counts accident cases. Prior-year (FY 2023-24) counts held in Calculations > Accidents.

## Source_Gaps
Item | Gap (as of Pass 1) | Follow-up
Amendments / replacement regulation | Only the 1st Amendment (2010, S2) was found. No later amendment, replacement regulation or Commission order under Reg. 4(3) altering Schedules I-II was found in the repository; applicability of S1 as amended by S2 to FY 2024-25 rests on that basis. | Pass 2: confirm whether any amendment, replacement or Reg. 4(3) order was in force during FY 2024-25.
Reliability targets | No Commission notification of target levels for SAIFI / SAIDI / MAIFI (S1 Sch. II 1.5(ii)) applicable to FY 2024-25 was found; the S3 target column is blank for these rows. | Pass 2: search OERC orders for reliability targets.
Licensee's own SoP returns | TPWODL's monthly Guaranteed Standards reports and quarterly / annual Overall Standards reports (S1 Reg. 6) are not in the repository; only the Commission's consolidated annual statement (S3) is available. Case counts behind the reported shares are therefore unavailable. | Pass 2: locate TPWODL SoP returns for FY 2024-25.
Guaranteed Standards performance | S3 Note 1 states that Guaranteed Standards information is available on the OERC and licensee websites; no such document is in the repository. | Pass 2: obtain Guaranteed Standards performance for FY 2024-25.
Reliability-index disaggregation | S1 requires monthly indices, urban/rural segregation and separate indices for predominantly agricultural feeders; only single annual values are reported, and whether agricultural feeders are excluded is not stated. | Pass 2: locate monthly and disaggregated indices.
Frequency, street-light and EHT voltage values | S3 shows '--' for TPWODL for supply frequency and '-' for street-light rectification and EHT voltage in FY 2024-25 (frequency and street-light also unreported in earlier years); no explanation is given. | Pass 2: check licensee returns.
Voltage unbalance and harmonics | No reported values for S1 Sch. II 1.7 (voltage unbalance) or Sch. I 2.2 (harmonics); Commission orders setting the harmonics stage dates were not found. | Pass 2: locate data and orders.
Compensation records | No data on compensation paid under S1 Reg. 5 / Sch. III. | Pass 2: locate compensation data.
Referenced instruments | Orissa Grid Code (harmonics), OERC Distribution (Conditions of Supply) Code, 2004 (meters, new connections), Indian Electricity Rules, 1956 (S3 voltage row; S1 Sch. II 1.6) and the Government of Orissa rural-areas notification of 30 March 2005 (S2) are not in the repository. | Pass 2: obtain if needed for definitions.
S2 gazette date | S2 states it comes into force on publication in the Official Gazette; the gazette date is not in the file. | Pass 2: confirm publication date (before FY 2024-25 in any case, as notified December 2010).
DISCOM full name | The permitted sources identify the licensee only as 'TPWODL' (and the website tpwesternodisha.com); the full registered name is not stated. | Pass 2: confirm full name and update the DISCOM field.
Drive links | Files were supplied without Google Drive URLs; the connected Google Drive was searched and holds no TPWODL or OERC documents. Link fields are recorded as not available. | Add Drive links when available.
Unit of voltage-case value | The FY 2024-25 HT value (0.08) is fractional, as the FY 2022-23 value (1.5) was; the FY 2023-24 value (9) was a whole number. Whether the value is a count, an average or another measure is not stated. No licensee return or Commission format explaining the reported basis is in the repository. | Pass 2: locate the licensee return or Commission reporting format.
Scale of billing and meter shares | S3 prints faulty-bill and defective-meter shares as 0.00% and 0.05%, far below the FY 2021-22 values (0.10 and 5) and varying by orders of magnitude between years (meters: 5, 0.0013, 0.0836, 0.05); no licensee return explaining the scale is in the repository. | Pass 2: check licensee returns.

## Data_Quality_Flags
Item | Observation | Treatment
Defective-meter share | TPWODL reports 0.05% (FY 2023-24: 0.0836; FY 2022-23: 0.0013; FY 2021-22: 5). The FY 2024-25 value carries a percent sign. Other licensees report 0.23% to 1.20% in the same row. | Read as per cent as printed; below the 5% ceiling; scale of the series flagged.
Faulty-bill share | TPWODL reports 0.00% (FY 2023-24: 0.0005; FY 2022-23: 0.0004; FY 2021-22: 0.10). Other licensees report 0.00% to 1.66%. The 1.66% (TPNODL) is above the 0.1% ceiling but is not a TPWODL figure. | Read as per cent as printed; below the 0.1% ceiling.
Distribution-transformer shares | Urban 96.39% and rural 85.01% (FY 2023-24: 98.70% / 85.75%). The S1 threshold of 95% applies to total DTs failed; case counts are not reported. The rural share is below 95% and the urban share above it. | Aggregate compliance not determinable without case counts; comparison marked not possible; see Review_Items.
Line-breakdown shares | Urban 100.00% and rural 100.00% (FY 2023-24: 99.96% / 100.00%). Both exceed the 95% threshold; the clock-start difference between S1 (occurrence of breakdown) and S3 (receipt of complaint) is unchanged. | Comparison marked not possible; combined share equals 100% because both area shares are equal.
Voltage values | HT 0.08 and LT 0 under a 'No. of cases' label; EHT '-'. The HT value is fractional (FY 2023-24: 9; FY 2022-23: 1.5). Other licensees show EHT, HT and LT values in the same block. | Presented as printed with unit not established; comparison not possible.
Voltage row wording | The row reads 'exceeded 3% of the voltage limits'. S1 sets voltage limits of +6/-6% (LV), +6/-9% (HV), +10/-12.5% (EHV) and a separate 3% voltage-unbalance limit. | Definitional mismatch recorded; no benchmark comparison made.
Scheduled-outage share | TPWODL reports 100.00% against a minimum target of 90 for 'completing the work within 12 hrs. of the scheduled outage before 5 PM/6 PM'. S1 Sch. II 1.4 combines advance notice, a daily duration cap of 12 hours and restoration by 6 p.m. (summer) / 5 p.m. (winter). | Comparison marked not possible; see Review_Items.
S1 Sch. II 1.1 cross-reference | Sch. II 1.1 refers to the time limits in 'sub-paragraph 1.1 of Schedule-I', which concerns information on likely restoration time; the fuse-off time limits are in Sch. I 1.2. S3 applies the Sch. I 1.2 limits (6 / 24 hours). | Sch. I 1.2 time limits applied as the fuse-off time standard.
Billing-mistake wording | S1: 'bills requiring rectifications following complaints'; S3: 'faulty bills prepared'. Any bill requiring rectification after a complaint is a faulty bill, so the S3 share is not lower than the S1 share. | Treated as the same parameter.
Area terminology | S1 uses 'towns and cities' and 'rural areas'; S3 uses 'urban areas' and 'rural areas'; S2 defines Urban Areas as areas under NAC, Municipality and Municipal Corporation. | Treated as the same urban/rural classification.
Momentary-interruption threshold | S1 defines momentary as <= 5 minutes and sustained as > 5 minutes; S3 labels MAIFI 'less than 5 minutes' and SAIFI 'more than 5 minutes'. | Treated as the S1 definitions; flagged.
Reliability-index precision and weighting | SAIFI, MAIFI and SAIDI are reported as whole numbers and are weighted by connected load (kW), not by number of consumers. Labels are unchanged from earlier years. | Presented at source precision; unit stated per kW of connected load.
Large year-on-year changes | TPWODL accident cases: fatal human 46 to 8, fatal animal 46 to 28, non-fatal human 44 to 12. SAIDI 18,312 to 20,684; SAIFI 428 to 424; MAIFI 43 to 62. | Reported as published; FY 2023-24 accident values in S3 agree with the FY 2023-24 workbook (continuity check).
S3 document form | S3 is a single-page Commission statement; it carries a reference number (OERC.-11011(11)/1/2026-ENGG DIV-OERC I/21639/2026) but no issue date. Accident counts are printed with leading zeros; share values carry percent signs. | Recorded in Source_Documentation.

## Review_Items
Item | Summary | Reason held for review
Distribution-transformer compliance basis | S1 sets one aggregate threshold (95%) over total DTs failed. S3 shows the target against each area; the rural share (85.01%) is below it and the urban share (96.39%) above it. The dashboard marks the row not comparable because the aggregate cannot be determined without case counts; an area-by-area reading would show the rural share below the target. | Methodological judgement; same treatment as FY 2023-24; obtain case counts in Pass 2.
Line-breakdown comparability | S3 presents the shares against the Commission's minimum target (95). The dashboard treats them as not comparable because the reported time is measured from receipt of complaint rather than from occurrence of the breakdown, even though both shares (100.00%) exceed the target. | Methodological judgement; same treatment as earlier years; confirm the licensee's measurement basis in Pass 2.
Scheduled-outage comparability | S3 reports 100.00% against a minimum target of 90. Treated as not comparable because the standard also requires advance notice and a daily duration cap. | Methodological judgement; same treatment as FY 2023-24.
Voltage-case unit | HT 0.08 is fractional, so it cannot be confirmed as a count of cases. LT is 0 and EHT is not reported. | Confirm the unit in Pass 2 (licensee return or Commission format).
Billing and meter share scale | Values (0.00%, 0.05%) are printed with percent signs and meet the ceilings, but the series differs by orders of magnitude from year to year. | Confirm in Pass 2 (licensee return).
Street-light rectification and supply frequency | No value reported for FY 2024-25 (as in earlier years). | Revisit if Pass 2 locates a value and the licensee's measurement basis.
CAIDI | Not specified in S1 and not reported in S3. | Not included in the main dataset.
Accident counts | S3 shows FY 2023-24 counts (FH 46, FA 46, NFH 44, NFA 0), matching the FY 2023-24 workbook. S1 Sch. II 1.11 treats change over time as an indicator, without a target. | Held in Calculations > Accidents; continuity confirmed.
Guaranteed Standards and compensation | Schedule I event-level standards and Schedule III compensation have no reported data for FY 2024-25 in the repository. | Source gap; add rows if Pass 2 locates data.

## Conventions
Convention | Rule
Category convention | Supply-restoration and fault-rectification shares, billing mistakes and defective meters = Quality of Service; reliability indices, supply frequency and supply voltage = Quality & Reliability of Supply; accidents = Safety.
Indicator naming | '<Service> — share resolved within standard' for time-limited restoration parameters; '<Parameter> — <ratio>' for ratio standards; reliability indices use the full name with abbreviation; accidents follow 'Fatal / Non-fatal electrical accidents — humans / animals'.
Urban / rural | Where the standard and the reported data distinguish urban and rural areas, both appear in one row: area shares in Reported data; the combined FY share in the annualised field only where it can be derived without case counts (both area shares equal).
Percentages | One decimal place in the annualised field, e.g., 100.0%; Reported data retain source precision (e.g., 100.00%, 96.39%). Exception: faulty-bill and defective-meter shares are kept at source precision (0.00%, 0.05%) because one-decimal rounding would show 0.0% or 0.1% and obscure the value.
Indices | SAIDI in minutes, SAIFI in interruptions and MAIFI in momentary interruptions, each per kW of connected load (connected-load weighting per S1). Values are reported as annual whole numbers and are presented at source precision rather than two decimals.
FY notation | 'FY 2024-25' (April 2024 to March 2025).
Reported data | Final metric or concise series only, preserving the annual reporting basis and the urban/rural split; 'No value reported for FY 2024-25.' where the source shows '--'.
Annualised field | 'FY <metric>: <value>.'; 'Not annualised: no reported value.' where no value is reported; 'Not annualised: case counts required to combine the urban and rural shares are not reported.' where area shares differ and no counts are available; 'FY HT value: <value>; LT value: <value> (unit not established).' for the voltage row.
Comparison rule | Comparison possible? = No => Standard met? = N/A, without exception. Yes only where definition, unit, period, area and aggregation level align and the result can be determined on the original regulatory basis (aggregate share over total cases); where urban and rural shares fall on different sides of the threshold and case counts are unavailable the result cannot be determined and the row is marked No.
Reference workbooks | TPWODL FY 2023-24 dashboard and calculations workbooks used as the primary template for format, naming, units, precision and structure; UGVCL FY 2024-25 workbooks as the wider dashboard reference. Neither used as evidence; all FY 2024-25 evidence re-established from the current sources.