## Main
State | DISCOM | Financial year | Indicator category | Indicator | Standard | Reported data | Annualised / standardised reported data | Comparison possible? | Standard met? | If comparison is not possible, why? | Interpretation | Documentation of standardisation / transformation
Odisha | TP Western Odisha Distribution Limited (TPWODL) | FY 2022-23 | Quality of Service | Normal fuse-off call rectification — share resolved within standard | At least 90% of fuse-off calls rectified within 6 hours (Urban) / 24 hours (Rural) of complaint | Within-standard share (FY, annual reporting): Urban 100.00%; Rural 100.00%. | FY within-standard share: 100.0%. | Yes | Yes | Not applicable. | Performance met the applicable regulatory standard. | FY share for urban and rural areas combined derived from the two reported area shares, which are both 100.00%, so the result does not depend on the unreported case counts; reported on an annual basis, so no annualisation was required.
Odisha | TP Western Odisha Distribution Limited (TPWODL) | FY 2022-23 | Quality of Service | Line breakdown restoration — share resolved within standard | At least 95% of line breakdowns restored within 12 hours (Urban) / 24 hours (Rural) of occurrence of the breakdown | Within-standard share (FY, annual reporting; time measured from receipt of complaint): Urban 100.00%; Rural 100.00%. | FY within-standard share (time measured from receipt of complaint): 100.0%. | No | N/A | The standard measures restoration time from the occurrence of the breakdown, while the reported share measures it from receipt of the complaint, which may be later; the reported share therefore does not measure performance against the regulatory time limit. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY share for urban and rural areas combined derived from the two reported area shares, which are both 100.00%, so the result does not depend on the unreported case counts; reported on an annual basis, so no annualisation was required.
Odisha | TP Western Odisha Distribution Limited (TPWODL) | FY 2022-23 | Quality of Service | Distribution transformer failure restoration — share resolved within standard | At least 95% of failed distribution transformers replaced within 24 hours (Urban) / 48 hours (Rural) of complaint | Within-standard share (FY, annual reporting): Urban 99.08%; Rural 97.33%. | Not annualised: case counts required to combine the urban and rural shares are not reported. | Yes | Yes | Not applicable. | Performance met the applicable regulatory standard. | Combined urban and rural share not derived because case counts are not reported; compliance established because both area shares exceed the 95% threshold, so any combination of them also exceeds it; reported on an annual basis, so no annualisation was required.
Odisha | TP Western Odisha Distribution Limited (TPWODL) | FY 2022-23 | Quality of Service | Scheduled outage restoration — share resolved within standard | At least 90% of scheduled outages notified in advance (at least 24 hours), not exceeding 12 hours a day, and with supply restored by 6 p.m. (summer) / 5 p.m. (winter) | Within-standard share (FY, annual reporting): 100.00%. | FY within-standard share: 100.0%. | No | N/A | The standard requires advance notice (at least 24 hours), a duration of not more than 12 hours a day and restoration by 6 p.m. (summer) / 5 p.m. (winter), each in at least 90% of cases, while the reported share is defined only as work completed within 12 hours of the scheduled outage before 5 p.m. / 6 p.m.; it does not cover advance notice or state the season-specific restoration time. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | None; reported on an annual basis, so no annualisation was required.
Odisha | TP Western Odisha Distribution Limited (TPWODL) | FY 2022-23 | Quality of Service | Street-light fault rectification — share resolved within standard | At least 90% of street-light faults rectified within 6 hours of detection or complaint, whichever is earlier | No value reported for FY 2022-23. | Not annualised: no reported value. | No | N/A | No reported value is available for FY 2022-23. | Direct comparison is not possible because no reported value is available. | Not annualised because no reported value is available.
Odisha | TP Western Odisha Distribution Limited (TPWODL) | FY 2022-23 | Quality of Service | Billing mistakes — faulty bills as share of bills issued | Bills requiring rectification following complaints not more than 0.1% of bills issued | Faulty bills as a share of bills issued (FY, annual reporting): 0.0004%. | FY faulty-bill share: 0.0004%. | Yes | Yes | Not applicable. | Performance met the applicable regulatory standard. | None
Odisha | TP Western Odisha Distribution Limited (TPWODL) | FY 2022-23 | Quality of Service | Defective meters — share of meters in service | Defective meters not more than 5% of meters in service | Defective meters as a share of meters in service (FY, annual reporting): 0.0013%. | FY defective-meter share: 0.0013%. | Yes | Yes | Not applicable. | Performance met the applicable regulatory standard. | None
Odisha | TP Western Odisha Distribution Limited (TPWODL) | FY 2022-23 | Quality & Reliability of Supply | System Average Interruption Duration Index (SAIDI) | No quantitative benchmark specified (target levels may be notified by the Commission annually under the regulation) | Annual SAIDI (minutes per kW of connected load): 19,770. | FY SAIDI: 19,770 minutes per kW of connected load. | No | N/A | No quantitative reliability target applicable to FY 2022-23 is available; the regulation provides for the Commission to notify target levels annually. In addition, the regulation requires the indices to be computed monthly and reported separately for urban and rural feeders, while only a single annual value is reported, without monthly, urban/rural or agricultural-feeder disaggregation. | No quantitative regulatory benchmark is specified for direct comparison. | None
Odisha | TP Western Odisha Distribution Limited (TPWODL) | FY 2022-23 | Quality & Reliability of Supply | System Average Interruption Frequency Index (SAIFI) | No quantitative benchmark specified (target levels may be notified by the Commission annually under the regulation) | Annual SAIFI (interruptions per kW of connected load): 468. | FY SAIFI: 468 interruptions per kW of connected load. | No | N/A | No quantitative reliability target applicable to FY 2022-23 is available; the regulation provides for the Commission to notify target levels annually. In addition, the regulation requires the indices to be computed monthly and reported separately for urban and rural feeders, while only a single annual value is reported, without monthly, urban/rural or agricultural-feeder disaggregation. | No quantitative regulatory benchmark is specified for direct comparison. | None
Odisha | TP Western Odisha Distribution Limited (TPWODL) | FY 2022-23 | Quality & Reliability of Supply | Momentary Average Interruption Frequency Index (MAIFI) | No quantitative benchmark specified (target levels may be notified by the Commission annually under the regulation) | Annual MAIFI (momentary interruptions per kW of connected load): 40. | FY MAIFI: 40 momentary interruptions per kW of connected load. | No | N/A | No quantitative reliability target applicable to FY 2022-23 is available; the regulation provides for the Commission to notify target levels annually. In addition, the regulation requires the indices to be computed monthly and reported separately for urban and rural feeders, while only a single annual value is reported, without monthly, urban/rural or agricultural-feeder disaggregation. | No quantitative regulatory benchmark is specified for direct comparison. | None
Odisha | TP Western Odisha Distribution Limited (TPWODL) | FY 2022-23 | Quality & Reliability of Supply | Supply frequency outside ±3% of 50 Hz — number of hourly measurements | Licensee to endeavour to maintain supply frequency within ±3% of 50 Hz and report the number of hourly measurements outside this range; no numerical target specified | No value reported for FY 2022-23. | Not annualised: no reported value. | No | N/A | The regulation does not specify a quantitative benchmark for the number of supply-frequency excursions, and no reported value is available for FY 2022-23. | No quantitative regulatory benchmark is specified for direct comparison. | Not annualised because no reported value is available.
Odisha | TP Western Odisha Distribution Limited (TPWODL) | FY 2022-23 | Quality & Reliability of Supply | Supply voltage at point of supply outside limits — number of cases (EHT / HT / LT) | +6% / −6% (LV); +6% / −9% (HV); +10% / −12.5% (EHV) of declared voltage | Number of cases (HT, FY, annual reporting): 1.5; no value reported for EHT or LT. | FY HT value: 1.5 (unit not established). | No | N/A | The reported HT value (1.5) is fractional, so it cannot be confirmed as a count of cases, and no unit could be established from the regulation; in addition, the standard applies to the voltage at each consumer's point of supply, and no aggregate threshold for the number of cases outside the limits is specified. | Direct comparison is not possible because the unit of the reported value could not be established and no aggregate benchmark is specified. | None; reported on an annual basis, so no annualisation was required.
Odisha | TP Western Odisha Distribution Limited (TPWODL) | FY 2022-23 | Safety | Fatal electrical accidents — humans | No quantitative benchmark specified | Number of accidents (FY): 2. | FY fatal human accidents: 2. | No | N/A | The applicable regulation does not specify a quantitative benchmark for the number of electrical accidents; it identifies the change in the number of accidents over time as an indicator of performance, without a target. | No quantitative regulatory benchmark is specified for direct comparison. | None
Odisha | TP Western Odisha Distribution Limited (TPWODL) | FY 2022-23 | Safety | Non-fatal electrical accidents — humans | No quantitative benchmark specified | Number of accidents (FY): 24. | FY non-fatal human accidents: 24. | No | N/A | The applicable regulation does not specify a quantitative benchmark for the number of electrical accidents; it identifies the change in the number of accidents over time as an indicator of performance, without a target. | No quantitative regulatory benchmark is specified for direct comparison. | None
Odisha | TP Western Odisha Distribution Limited (TPWODL) | FY 2022-23 | Safety | Fatal electrical accidents — animals | No quantitative benchmark specified | Number of accidents (FY): 24. | FY fatal animal accidents: 24. | No | N/A | The applicable regulation does not specify a quantitative benchmark for the number of electrical accidents; it identifies the change in the number of accidents over time as an indicator of performance, without a target. | No quantitative regulatory benchmark is specified for direct comparison. | None
Odisha | TP Western Odisha Distribution Limited (TPWODL) | FY 2022-23 | Safety | Non-fatal electrical accidents — animals | No quantitative benchmark specified | Number of accidents (FY): 0. | FY non-fatal animal accidents: 0. | No | N/A | The applicable regulation does not specify a quantitative benchmark for the number of electrical accidents; it identifies the change in the number of accidents over time as an indicator of performance, without a target. | No quantitative regulatory benchmark is specified for direct comparison. | None
Note on B2: DISCOM field now gives the registered name with its abbreviation, as in the FY 2021-22 dataset and the reference workbook. Name from the TPWODL licence conditions, cl. 1.1 and 3.3(x) (S9).
Note on B3: DISCOM field now gives the registered name with its abbreviation, as in the FY 2021-22 dataset and the reference workbook. Name from the TPWODL licence conditions, cl. 1.1 and 3.3(x) (S9).
Note on B4: DISCOM field now gives the registered name with its abbreviation, as in the FY 2021-22 dataset and the reference workbook. Name from the TPWODL licence conditions, cl. 1.1 and 3.3(x) (S9).
Note on B5: DISCOM field now gives the registered name with its abbreviation, as in the FY 2021-22 dataset and the reference workbook. Name from the TPWODL licence conditions, cl. 1.1 and 3.3(x) (S9).
Note on B6: DISCOM field now gives the registered name with its abbreviation, as in the FY 2021-22 dataset and the reference workbook. Name from the TPWODL licence conditions, cl. 1.1 and 3.3(x) (S9).
Note on B7: DISCOM field now gives the registered name with its abbreviation, as in the FY 2021-22 dataset and the reference workbook. Name from the TPWODL licence conditions, cl. 1.1 and 3.3(x) (S9).
Note on B8: DISCOM field now gives the registered name with its abbreviation, as in the FY 2021-22 dataset and the reference workbook. Name from the TPWODL licence conditions, cl. 1.1 and 3.3(x) (S9).
Note on B9: DISCOM field now gives the registered name with its abbreviation, as in the FY 2021-22 dataset and the reference workbook. Name from the TPWODL licence conditions, cl. 1.1 and 3.3(x) (S9).
Note on B10: DISCOM field now gives the registered name with its abbreviation, as in the FY 2021-22 dataset and the reference workbook. Name from the TPWODL licence conditions, cl. 1.1 and 3.3(x) (S9).
Note on B11: DISCOM field now gives the registered name with its abbreviation, as in the FY 2021-22 dataset and the reference workbook. Name from the TPWODL licence conditions, cl. 1.1 and 3.3(x) (S9).
Note on B12: DISCOM field now gives the registered name with its abbreviation, as in the FY 2021-22 dataset and the reference workbook. Name from the TPWODL licence conditions, cl. 1.1 and 3.3(x) (S9).
Note on B13: DISCOM field now gives the registered name with its abbreviation, as in the FY 2021-22 dataset and the reference workbook. Name from the TPWODL licence conditions, cl. 1.1 and 3.3(x) (S9).
Note on B14: DISCOM field now gives the registered name with its abbreviation, as in the FY 2021-22 dataset and the reference workbook. Name from the TPWODL licence conditions, cl. 1.1 and 3.3(x) (S9).
Note on B15: DISCOM field now gives the registered name with its abbreviation, as in the FY 2021-22 dataset and the reference workbook. Name from the TPWODL licence conditions, cl. 1.1 and 3.3(x) (S9).
Note on B16: DISCOM field now gives the registered name with its abbreviation, as in the FY 2021-22 dataset and the reference workbook. Name from the TPWODL licence conditions, cl. 1.1 and 3.3(x) (S9).
Note on B17: DISCOM field now gives the registered name with its abbreviation, as in the FY 2021-22 dataset and the reference workbook. Name from the TPWODL licence conditions, cl. 1.1 and 3.3(x) (S9).

## Source_Documentation
ID | Source type | Source file name | Document title | Issuing authority | Publication / FY | Page(s) | Section / table / annexure | Google Drive link | Source note | Web URL | Sources folder: additional upload required?
S1 | Regulatory | Odisha_Principal_Regulation_2004.pdf | Orissa Electricity Regulatory Commission (Licensees' Standards of Performance) Regulations, 2004, Notification No. OERC-Engg-94/2003, dated 21 May 2004 | Orissa Electricity Regulatory Commission | Orissa Gazette Extraordinary No. 711, 28 May 2004; in force from publication (Reg. 1(4)); applicable throughout FY 2022-23 as amended by S2 | p.2 (Regs. 1-2); p.3 (Regs. 2-4); pp.4-5 (Regs. 5-6); pp.5-6 (Regs. 8-12); pp.7-13 (Schedule I); pp.14-16 (Schedule II); pp.17-19 (Schedule III) | Regs. 1-12; Schedule I (Guaranteed Standards); Schedule II (Overall Standards, incl. 1.5 reliability-index formulas, p.15); Schedule III (compensation) | Not available: file supplied in the permitted repository without a Google Drive URL | Applicable regulation for FY 2022-23. Source of all overall standards, thresholds, reliability-index formulas (connected-load weighted) and the accident provision. No repeal or replacement located in the permitted repository. Re-checked for FY 2022-23: no repeal, replacement or later amendment located in the permitted repository. Applicability for FY 2022-23 re-checked on OERC listings (S11, S12): the regulation appears with one amendment (S2) and no later final amendment. An OERC notice dated 22 September 2022 (S6), within FY 2022-23, states the regulations still required amendment because of the Electricity (Rights of Consumers) Rules, 2020 (S5), so they had not been replaced by then. Draft amendments (2019, 2025) are not final and were not used. | OERC (old site) copy: Licensees' Standards of Performance Regulations, 2004 | No. Supplied repository file (Odisha_Principal_Regulation_2004.pdf); presumed already in the Sources folder, which could not be inspected. The web URL is a second copy for reference only.
S2 | Regulatory | Odisha_1st_Amendment_2010.pdf | Orissa Electricity Regulatory Commission (Licensee's Standard of Performance) (1st Amendment) Regulations, 2010, Notification No. OERC-Engg.-94/2003(Vol.-III)/5584, dated 16 December 2010 | Orissa Electricity Regulatory Commission | Notified 16 December 2010; in force from publication in the Official Gazette (gazette date not stated in the file); applicable throughout FY 2022-23; Gazette No. 313 dated 04-02-2011 (per OERC regulations listing, S12) | pp.1-3 | Clauses 1-6: Reg. 3(2)-3(8) (call centres; definition of Urban Areas); new Reg. 8 (third-party audit); renumbering of Regs. 8-12 as 9-13; amended Reg. 9(1) (force majeure); new Schedule I clause 3.8 (temporary supply) | Not available: file supplied in the permitted repository without a Google Drive URL | Reviewed. Does not amend the Schedule II overall standards or the reliability-index formulas. Urban Areas definition (p.1) used to confirm that 'towns and cities' (S1) and 'urban areas' (S3) refer to the same area classification. Re-checked for FY 2022-23: no repeal, replacement or later amendment located in the permitted repository. | OERC copy: Licensee's Standard of Performance (1st Amendment) Regulations, 2010 | No. Supplied repository file (Odisha_1st_Amendment_2010.pdf); presumed already in the Sources folder, which could not be inspected.
S3 | Reported performance | Overall_Standards_of_Performance_1.pdf | Performance of Electricity Distribution Companies in Odisha during the FY 2022-23 (as reported and furnished through an affidavit): Achievement on Overall Standards of Performance | Odisha Electricity Regulatory Commission (data furnished by the distribution licensees through affidavit) | FY 2022-23 (annual values; accident counts also shown for FY 2021-22) | p.1 (single page) | Single table; TPWODL column ('For the year 2022-23'); column 'Minimum % target fixed by the Commission'; accident table (21-22 / 22-23); Notes 1-2 | Not available: file supplied in the permitted repository without a Google Drive URL | Reported annual performance for TPWODL. SAIFI/MAIFI unit '(Nos.)' and SAIDI unit '(Minutes)' stated in the parameter labels, each 'faced by 1 KW connected load'; weighting confirmed against S1 Schedule II formulas. TPWODL column alignment verified on a rendered image of the page. The FY 2021-22 statement for the same licensee is a separate document with the same layout; it is used here only for the continuity check in the calculations workbook. | Not available: no public web copy of the FY 2022-23 statement was located; the second-source value check could not be made | No. Supplied repository file (Overall_Standards_of_Performance_1.pdf) holds the reported values; presumed already in the Sources folder, which could not be inspected.
S5 | Regulatory | Web source: Gazette_Electricity-Rights-of-Consumers-Rules-2020 | The Electricity (Rights of Consumers) Rules, 2020 | Ministry of Power, Government of India | G.S.R. 818(E), 31 December 2020; in force on publication | Not established | Rule 10 (reliability parameters incl. SAIDI, SAIFI to be specified by the Commission) | Not available: web source; not yet uploaded to the permitted Drive repository | Final central rules in force throughout FY 2022-23. They require the State Commission to specify SAIDI / SAIFI parameters; no OERC instrument doing so was located, so the reliability benchmark stays unresolved. Copy hosted by the Maharashtra Electricity Regulatory Commission; an official gazette hosting page was not located. | Gazette copy hosted by MERC (PDF) | YES. Substantiates the statement in the SAIDI / SAIFI / MAIFI Standard cells that no Commission-specified reliability benchmark is available. Identified in the FY 2021-22 review; presence in the Sources folder cannot be verified (folder not located). Needed for FY 2022-23 as well; not a new requirement if already uploaded.
S6 | Regulatory (applicability evidence) | Web source: OERC public notice and EoI | OERC public notice and Expression of Interest: Consultancy for framing draft Distribution (Conditions of Supply) Code and draft Licensees' Standards of Performance Regulations | Odisha Electricity Regulatory Commission | 22 September 2022 (within FY 2022-23) | Not established | Terms of Reference | Not available: web source; not yet uploaded to the permitted Drive repository | Not a regulation. Evidence only that the 2004 regulations (as amended in 2010) had not been replaced by 22 September 2022, when the Commission stated they 'require amendment because of the Electricity (Rights of Consumers) Rules, 2020'. Applicability for the rest of FY 2022-23 rests on S11 and S12, which list no later final amendment. | OERC notice and EoI (PDF) | YES. Substantiates the applicability of the 2004 regulation, as amended, during FY 2022-23. Identified in the FY 2021-22 review; presence in the Sources folder cannot be verified (folder not located). Needed for FY 2022-23 as well; not a new requirement if already uploaded.
S7 | Regulatory | Web source: Compensation to Victims of Electrical Accidents.pdf | OERC (Compensation to Victims of Electrical Accidents) Regulation, 2020 | Odisha Electricity Regulatory Commission | 2020; in force on publication in the Odisha Gazette (cl. 1.4) | Not established | Cls. 9 and 12 (accident reports; monthly return to the Commission) | Not available: web source; not yet uploaded to the permitted Drive repository | Listed as a gazette notification on the OERC old-site regulations page (S12); the document states neither a gazette number nor a date, so its legal status rests on that listing. Used only for the reporting basis of accident records. It does not define fatal or non-fatal accidents and sets no benchmark. | OERC copy (PDF) | YES. Substantiates the reporting basis of the four accident rows. Identified in the FY 2021-22 review; presence in the Sources folder cannot be verified (folder not located). Needed for FY 2022-23 as well; not a new requirement if already uploaded.
S9 | Licence | Web source: TPWODL_Licence Condition-Final.pdf | Conditions of the distribution and retail supply licence of TP Western Odisha Distribution Limited (TPWODL) | Odisha Electricity Regulatory Commission | Conditions effective 1 January 2021 (cl. 1.1); 25 years (cl. 4.1) | Not established | Cls. 1.1, 3.3(x) | Not available: web source; not yet uploaded to the permitted Drive repository | Confirms the registered name; the licence applies for the whole of FY 2022-23. | OERC copy of licence conditions (PDF) | No. Used solely to establish the DISCOM's name.
S11 | Regulatory listing | Web page: OERC current regulations (CGRF and Distribution Licensee Obligation) | OERC Current Regulations: CGRF & Distribution Licensee Obligation | Odisha Electricity Regulatory Commission | Page consulted October 2026 | Not applicable | Listing | Not available: web source; not yet uploaded to the permitted Drive repository | Lists the Licensees' Standards of Performance Regulations, 2004 and the 2010 amendment and no other standards of performance entry. | OERC regulations page | YES (hosting page; a listing page has no direct document link). Substantiates that no later final amendment was listed. Identified in the FY 2021-22 review; presence in the Sources folder cannot be verified (folder not located). Needed for FY 2022-23 as well; not a new requirement if already uploaded.
S12 | Regulatory listing | Web page: OERC old-site regulations listing | OERC old-site regulations page | Odisha Electricity Regulatory Commission | Page consulted October 2026 | Not applicable | Listing | Not available: web source; not yet uploaded to the permitted Drive repository | Gives Gazette No. 313 dated 04-02-2011 for the 2010 amendment, lists the 2020 accident-compensation regulation as a gazette notification, and lists no other amendment to the standards of performance regulations. | OERC old-site regulations page | YES (hosting page). Substantiates the gazette details of the 2010 amendment and the absence of other listed amendments. Identified in the FY 2021-22 review; presence in the Sources folder cannot be verified (folder not located). Needed for FY 2022-23 as well; not a new requirement if already uploaded.
S13 | Reported performance (Guaranteed Standards) | Web source: Guarenteed_Standards_of_Performance_22-23.pdf | Performance of Electricity Distribution Companies in Odisha during 2022-23 (based on the data furnished through affidavit): Guaranteed Standards | Odisha Electricity Regulatory Commission (copy hosted on a licensee website) | FY 2022-23; unresolved cases counted at 31.03.2023 | Not established | Items 1-12 (case counts per licensee) | Not available: web source; not yet uploaded to the permitted Drive repository | Located after the first review. Reports complaint counts received, resolved within time, beyond time and unresolved for each licensee. The table columns are garbled in the text available, so the TPWODL counts could not be read with confidence and are not used for any dashboard value. Recorded as an unresolved discrepancy in Review_Items. | Guaranteed Standards report FY 2022-23 (PDF, copy on a licensee website) | No. Not used in the final Main sheet: the counts could not be read reliably.
Note on J2: Applicability evidence for FY 2022-23 added from S6, S11 and S12. Drafts excluded.
Note on K2: Direct web copy of S1. Notification no. OERC-Engg-94/2003, 21 May 2004, Gazette Extraordinary No. 711 (28 May 2004) confirmed on the document.
Note on L2: Final Sources-folder check against the completed Main sheet.
Note on F3: Gazette number and date added from the OERC old-site listing (S12); the amendment document does not state them.
Note on K3: Direct OERC-hosted copy of S2; notification no. OERC-Engg.-94/2003(Vol.-III)/5584 dated 16 Dec 2010 confirmed.
Note on L3: Final Sources-folder check against the completed Main sheet.
Note on K4: Hosting limitation recorded: the only copy of this statement is the supplied file, so the TPWODL values rest on one copy (cross-licensee checks in Calculations > Threshold_Tests).
Note on L4: Final Sources-folder check against the completed Main sheet.
Note on A5: New source (S5) added; supports the changes noted in Main, Source_Gaps, Definitions_Units, Review_Items and the calculations workbook.
Note on A6: New source (S6) added; supports the changes noted in Main, Source_Gaps, Definitions_Units, Review_Items and the calculations workbook.
Note on A7: New source (S7) added; supports the changes noted in Main, Source_Gaps, Definitions_Units, Review_Items and the calculations workbook.
Note on A8: New source (S9) added; supports the changes noted in Main, Source_Gaps, Definitions_Units, Review_Items and the calculations workbook.
Note on A9: New source (S11) added; supports the changes noted in Main, Source_Gaps, Definitions_Units, Review_Items and the calculations workbook.
Note on A10: New source (S12) added; supports the changes noted in Main, Source_Gaps, Definitions_Units, Review_Items and the calculations workbook.
Note on A11: New source (S13) added; supports the changes noted in Main, Source_Gaps, Definitions_Units, Review_Items and the calculations workbook.

## Regulatory_Standards
Service / indicator | Area | Standard (original regulatory basis) | Source | Standard basis | Reporting format
Information on likely restoration time | All | Within 4 hours of complaint, on enquiry by the consumer | S1 Sch. I 1.1, p.7 | Event-level time standard | Not reported in S3
Normal fuse-off (supply restoration) | Urban / Rural | 6 hours (towns and cities); 24 hours (rural areas) from receipt of complaint (HG or LT fuses at the distribution transformer or consumer premises) | S1 Sch. I 1.2, p.7 | Event-level time standard | S3 p.1, rows 'Rectification of fuse-off call within 6 hrs. / 24 hrs.'
Normal fuse-off calls (overall) | All (total calls received) | Percentage of fuse-off calls rectified within the Schedule I time limits to total calls received not less than 90% | S1 Sch. II 1.1, p.14 (cross-refers to Sch. I sub-para 1.1; see Data_Quality_Flags) | Aggregate share threshold | S3 p.1, Urban and Rural rows; Commission's minimum target 90 shown for each area
Line breakdowns (supply restoration) | Urban / Rural | 12 hours (towns and cities); 24 hours (rural areas) from occurrence of breakdown; major breakdowns (heavy rain, lightning, whirlwind, needing conductor/structure replacement) 24 hours / 48 hours | S1 Sch. I 1.3, p.7 | Event-level time standard | S3 p.1 (measured 'of receiving the complaint')
Line breakdowns (overall) | Urban / Rural | Restoration within 12 hours (towns and cities) / 24 hours (rural areas) of occurrence of breakdown in at least 95% of cases | S1 Sch. II 1.2, p.14 | Aggregate share threshold | S3 p.1, Urban and Rural rows; minimum target 95
Distribution transformer failure (supply restoration) | Urban / Rural | Replacement within 24 hours (towns and cities); 48 hours (rural areas) of receiving the complaint | S1 Sch. I 1.4, p.7 | Event-level time standard | S3 p.1
Distribution transformer failures (overall) | All (total DTs failed) | Percentage of DTs replaced within the Schedule I time limits to total DTs failed not less than 95% | S1 Sch. II 1.3, p.14 | Aggregate share threshold | S3 p.1, Urban and Rural rows; minimum target 95
Scheduled outages | All | Notified at least 24 hours in advance; not more than 12 hours in a day; supply restored by 6 p.m. (summer) / 5 p.m. (winter) | S1 Sch. I 1.5, p.7 | Event-level | See next row
Scheduled outages (overall) | All | Both standards (duration and restoration time) achieved in at least 90% of cases | S1 Sch. II 1.4, p.14 | Aggregate share threshold | S3 p.1, row 'Completing the work within 12 hrs. of the scheduled outage before 5 PM/6 PM'; TPWODL 100.00; minimum target 90
Voltage variations | LV / HV / EHV | +6% / −6% (LV); +6% / −9% (HV); +10% / −12.5% (EHV) of declared voltage, at the point of commencement of supply; complaint: improve within 15 days (no network expansion), resolve within 120 days (up to 11 kV) / 180 days (up to 33 kV); intimate within 7 days if due to transmission | S1 Sch. I 2.1, p.8 | Point-of-supply limit; event-level complaint times | S3 p.1, row 'No. of cases in which voltage at the point of commencement of supply exceeded 3% of the voltage limits' (EHT/HT/LT); TPWODL HT 1.5, EHT and LT '--'
Harmonics | ≥132 kV / 33 kV / 11 kV consumers | THDv limited to 3% (132 kV and above), 8% (33 kV), 8% (11 kV) per Orissa Grid Code; Stage 1 effective on Commission order; Stages 2-3 dates to be set | S1 Sch. I 2.2, pp.8-9 | Point-of-supply limit (staged) | Not reported in S3
Meter complaints | All | Inspect within 7 working days; replace defective licensee meter within 30 days; burnt meter (not consumer-caused) within 30 working days; consumer-caused: notice within 7 days, replace within 15 days of payment | S1 Sch. I 2.3, p.9 | Event-level time standard | Not reported in S3
New connections / additional load | LT / HT / EHT | Notice within 3 days and estimate within one week (LT); feasibility 21/30 working days and estimate 60 working days (HT/EHT); supply within one month (no extension), 30/60/90 days (LT/11 kV/33 kV extension); temporary supply sanction within 3 days (Urban) / 7 days (Rural) | S1 Sch. I 3.1-3.7, pp.9-12; S2 cl. 6 (Sch. I 3.8), p.3 | Event-level time standard | Not reported in S3
Transfer of ownership and conversion of services | All | 15 days (title transfer, change of category); 30 / 60 / 90 days (LT 1-ph↔3-ph / LT↔11 kV / LT↔33 kV conversion) | S1 Sch. I 4, p.12 | Event-level time standard | Not reported in S3
Bill complaints and reconnection | All | Bill complaints resolved within 30 days; reconnection within 4 working hours of proof of payment | S1 Sch. I 5.1-5.2, p.13 | Event-level time standard | Not reported in S3
SAIFI / SAIDI / MAIFI | Licensee-wide 11 kV feeders excl. predominantly agricultural; agricultural feeders separately; urban / rural separately; monthly | Indices per IEEE 1366 (1998) computed with connected-load weighting: SAIFI = Σ(Ai×Ni) ÷ Nt; SAIDI = Σ(Bi×Ni) ÷ Nt; MAIFI = Σ(Ci×Ni) ÷ Nt (sustained > 5 minutes; momentary ≤ 5 minutes). No numeric target; the Commission may notify target levels annually | S1 Sch. II 1.5, pp.14-15 | None (target not available) | S3 p.1, annual values for TPWODL; target column blank; Rule 10 of the Electricity (Rights of Consumers) Rules, 2020 (S5) requires the Commission to specify SAIDI / SAIFI parameters; no OERC specification located
Supply frequency | All | Endeavour to maintain within ±3% of 50 Hz; hourly measurement; report number of events outside limits | S1 Sch. II 1.6, p.16 | No quantitative benchmark (reporting obligation) | S3 p.1; TPWODL '--'
Voltage unbalance | All | Not to exceed 3% at the point of commencement of supply; computation method to be specified separately | S1 Sch. II 1.7, p.16 | Point-of-supply limit | Not reported in S3
Street-light faults | All | Rectify line faults and restore street lights within 6 hours of detection or receipt of complaint, whichever is earlier, in at least 90% of cases | S1 Sch. II 1.8, p.16 | Aggregate share threshold | S3 p.1 (measured 'of receiving the complaint'); minimum target 90; TPWODL '--'
Billing mistakes | All | Percentage of bills requiring rectification following complaints to total bills issued not greater than 0.1% | S1 Sch. II 1.9, p.16 | Aggregate share ceiling | S3 p.1, row 'No. of faulty bills prepared as a percentage of total no. of bills issued'; minimum target column 0.1
Faulty meters | All | Percentage of defective meters to total meters in service not greater than 5% | S1 Sch. II 1.10, p.16 | Aggregate share ceiling | S3 p.1, row 'No. of faulty/defective meters as a percentage of total no. of existing meters'; minimum target column 5
Electrical accidents | All | Licensee to endeavour to minimise electrical accidents; increase or decrease over time is an indicator of performance. No numeric benchmark | S1 Sch. II 1.11, p.16 | No quantitative benchmark | S3 p.1, accident table (fatal / non-fatal, human / animal; 21-22 and 22-23); accident records and monthly returns to the Commission under cls. 9-12 of the OERC (Compensation to Victims of Electrical Accidents) Regulation, 2020 (S7)
Compensation to consumers | Urban / other areas | Schedule of compensation (Rs. 50 to Rs. 1,000 per case or per day of default; automatic or to be claimed) for failure to meet Guaranteed Standards | S1 Reg. 5; Sch. III, pp.17-19 | Compensation schedule | Not reported in S3
Reporting obligations | All | Guaranteed Standards: monthly reports within 15 days and annual report within 30 days of year-end. Overall Standards: quarterly reports within 15 days and annual report within 30 days of year-end | S1 Reg. 6(1)-6(4), pp.4-5 | Reporting basis | Only the Commission's consolidated annual statement (S3) is available
Force majeure exemption | All | Standards suspended during force majeure, including outages due to generation or transmission failure and outages initiated by NLDC / RLDC / SLDC | S1 Reg. 8(1) as renumbered and amended as Reg. 9(1) by S2 cl. 4-5, p.3 | Exemption | Application to reported values not stated in S3
Note on F17: Rule 10 of the 2020 Rules requires a Commission specification; none located, so the benchmark remains unresolved. Standard unchanged.
Note on F23: Reporting basis added from S7. No benchmark is set there; Standard unchanged.

## Definitions_Units
Indicator | Definition / formula | Dashboard unit | Reporting basis | Evidence | Note
Within-standard share (fuse-off, line breakdown, distribution transformer, scheduled outage, street light) | Cases rectified / restored / replaced within the Schedule I time limit ÷ total cases (calls received; DTs failed) × 100 | Percentage (%) | Annual (FY 2022-23), urban and rural reported separately for the first three parameters | S1 Sch. II 1.1-1.4, 1.8, p.14, p.16; S3 p.1 ('Achievement in %') | Underlying case counts are not reported. Line-breakdown rows in S3 measure time from receipt of complaint (S1: occurrence of breakdown). Scheduled-outage row in S3 is worded 'completing the work within 12 hrs. of the scheduled outage before 5 PM/6 PM' (S1 also requires advance notice and a daily duration cap). Street-light share not reported for FY 2022-23.
Faulty-bill share | Bills requiring rectification following complaints ÷ total bills issued × 100 (S1); 'faulty bills prepared as a percentage of total no. of bills issued' (S3) | Percentage (%) | Annual | S1 Sch. II 1.9, p.16; S3 p.1 | Reported to four decimal places (0.0004), labelled a percentage in S3; read as per cent. A reading as a fraction (0.04%) would not change the compliance result. Wording differs between S1 and S3; see Data_Quality_Flags. The other three licensees report 0.1, 1.49 and 0.14 in the same row of S3; TPWODL's 0.0004 is far below them.
Defective-meter share | Defective meters ÷ total meters in service × 100 | Percentage (%) | Annual (point in the year not stated) | S1 Sch. II 1.10, p.16; S3 p.1 | Reported to four decimal places (0.0013), labelled a percentage in S3; read as per cent. A reading as a fraction (0.13%) would not change the compliance result. The other three licensees report 1.36, 13 and 2.29 in the same row of S3 (13 exceeds the 5% ceiling), which is consistent with a per cent scale for the table; TPWODL's 0.0013 is far below them and its scale could not be explained from any source.
SAIDI | Σ(Bi×Ni) ÷ Nt; Bi = total duration of sustained interruptions on feeder i in the month; Ni = connected load of feeder i affected; Nt = total 11 kV connected load | Minutes per kW of connected load | Annual value | S1 Sch. II 1.5, p.15 (formula; duration unit not stated); S3 p.1 ('Total duration of interruption in minutes each 1 KW connected load (SAIDI)(Minutes)') | Connected-load weighted, not consumer weighted; not directly comparable with consumer-weighted indices of other states.
SAIFI | Σ(Ai×Ni) ÷ Nt; Ai = number of sustained interruptions (each longer than 5 minutes) on feeder i in the month | Interruptions per kW of connected load | Annual value | S1 Sch. II 1.5, p.15; S3 p.1 ('Total no. of interruption each lasting more than 5 minutes faced by 1 KW connected load (SAIFI)(Nos.)') | Unit derived from formula: (count × kW) ÷ kW = count per unit of connected load; S3 states '(Nos.)' per 1 kW.
MAIFI | Σ(Ci×Ni) ÷ Nt; Ci = number of momentary interruptions (each less than or equal to 5 minutes) on feeder i in the month | Momentary interruptions per kW of connected load | Annual value | S1 Sch. II 1.5, p.15; S3 p.1 ('... each lasting less than 5 minutes faced by 1 KW connected load (MAIFI)(Nos.)') | S1 momentary threshold '≤ 5 minutes'; S3 label 'less than 5 minutes'.
Supply-frequency excursions | Number of hourly measurements with supply frequency outside ±3% of 50 Hz | Number of hourly measurements (count) | Not reported | S1 Sch. II 1.6, p.16; S3 p.1 | No value reported.
Voltage cases outside limits | Number of cases in which voltage at the point of commencement of supply exceeded the limits (S3 wording: 'exceeded 3% of the voltage limits'; FY 2021-22 wording also cited 'I.E. Rules, 1956') | Unit not established (published as 'No. of cases'; reported HT value 1.5 is fractional) | Annual; HT value only | S1 Sch. I 2.1, p.8; S3 p.1 | Fractional value is inconsistent with a count of cases; no instruction on the unit or on the reporting basis was found in S1, S2 or S3. S3 wording does not correspond to the S1 voltage limits. The Guaranteed Standards report for FY 2022-23 (S13) counts voltage complaints, a different measure, and does not explain a fractional value.
Electrical accidents (fatal / non-fatal; human / animal) | Number of accident cases in the year | Number of accidents (count) | Annual | S3 p.1 ('No. of accident cases'); S1 Sch. II 1.11, p.16 | Counts accident cases. Prior-year (FY 2021-22) counts held in Calculations > Accidents. Records are kept and returned monthly to the Commission under cls. 9-12 of the 2020 compensation regulation (S7), which does not define fatal or non-fatal.
Note on F3: Cross-licensee scale evidence added (Calculations > Threshold_Tests). Unit reading and result unchanged.
Note on F4: Cross-licensee scale evidence added (Calculations > Threshold_Tests). Unit reading and result unchanged.
Note on F9: Searched for a unit explanation in S13; none found.
Note on F10: Reporting basis added (S7).

## Source_Gaps
Item | Gap | Follow-up | Status after further review | Evidence (link)
Amendments / replacement regulation | Only the 1st Amendment (2010, S2) was found. No later amendment, replacement regulation or Commission order under Reg. 4(3) altering Schedules I-II was found in the repository; applicability of S1 as amended by S2 to FY 2022-23 rests on that basis. | Pass 2: confirm whether any amendment, replacement or Reg. 4(3) order was in force during FY 2022-23. | Partly resolved. OERC's regulation listings show the 2004 regulation with the 2010 amendment only; no final later amendment or Reg. 4(3) order was located. An OERC notice of 22 September 2022 (S6) states the regulations still required amendment. Only draft amendments exist (below) and were not used. | OERC current regulations page (S11)
Reliability targets | No Commission notification of target levels for SAIFI / SAIDI / MAIFI (S1 Sch. II 1.5(ii)) applicable to FY 2022-23 was found; the S3 target column is blank for these rows. | Pass 2: search OERC orders for reliability targets. | Unresolved. Rule 10 of the Rights of Consumers Rules, 2020 (S5) requires the Commission to specify SAIDI / SAIFI parameters; no OERC instrument doing so was located. | Rights of Consumers Rules, 2020 (S5)
Licensee's own SoP returns | TPWODL's monthly Guaranteed Standards reports and quarterly / annual Overall Standards reports (S1 Reg. 6) are not in the repository; only the Commission's consolidated annual statement (S3) is available. Case counts behind the reported shares are therefore unavailable. | Pass 2: locate TPWODL SoP returns for FY 2022-23. | Partly located. The Commission's FY 2022-23 Guaranteed Standards report (S13) gives complaint counts by licensee, but the table could not be read reliably with the tools available; Overall Standards case counts were not obtained. | Guaranteed Standards report FY 2022-23 (S13)
Guaranteed Standards performance | S3 Note 1 states that Guaranteed Standards information is available on the OERC and licensee websites; no such document is in the repository. | Pass 2: obtain Guaranteed Standards performance for FY 2022-23. | Located but not used. See S13: counts for TPWODL could not be read reliably and are not used for any dashboard value (see Review_Items). | Guaranteed Standards report FY 2022-23 (S13)
Reliability-index disaggregation | S1 requires monthly indices, urban/rural segregation and separate indices for predominantly agricultural feeders; only single annual values are reported, and whether agricultural feeders are excluded is not stated. | Pass 2: locate monthly and disaggregated indices. | Unresolved. No monthly, urban / rural or agricultural-feeder indices located, and no Commission review note covering FY 2022-23 for TPWODL was located, so the reported SAIFI / SAIDI could not be cross-checked. Formula basis confirmed: S1 Sch. II 1.5 cites IEEE Std 1366 (1998). | S1 web copy
Frequency, street-light and EHT / LT voltage values | S3 shows '--' for TPWODL for supply frequency, street-light rectification and EHT and LT voltage; no explanation is given. | Pass 2: check licensee returns. | Unresolved. S3 shows '--' for TPWODL; no explanation located. | OERC Performance of Discoms page
Voltage unbalance and harmonics | No reported values for S1 Sch. II 1.7 (voltage unbalance) or Sch. I 2.2 (harmonics); Commission orders setting the harmonics stage dates were not found. | Pass 2: locate data and orders. | Unresolved. No TPWODL values or Commission orders located. | S1 web copy
Compensation records | No data on compensation paid under S1 Reg. 5 / Sch. III. | Pass 2: locate compensation data. | Unresolved. No compensation data located. | OERC Performance of Discoms page
Referenced instruments | Orissa Grid Code (harmonics), OERC Distribution (Conditions of Supply) Code, 2004 (meters, new connections), Indian Electricity Rules, 1956 (S3 voltage row; S1 Sch. II 1.6) and the Government of Orissa rural-areas notification of 30 March 2005 (S2) are not in the repository. | Pass 2: obtain if needed for definitions. | Partly resolved. The 2004 Supply Code was superseded by the Supply Code 2019 (OERC listing); no value or benchmark in the workbooks depends on it or on the Indian Electricity Rules 1956, the Orissa Grid Code or the 2005 rural-areas notification, which were not obtained. | OERC old-site regulations listing (S12)
S2 gazette date | S2 states it comes into force on publication in the Official Gazette; the gazette date is not in the file. | Pass 2: confirm publication date (before FY 2022-23 in any case, as notified December 2010). | Resolved. Gazette No. 313 dated 04-02-2011 per the OERC regulations listing (S12). Effective before FY 2022-23. | OERC old-site regulations listing (S12)
DISCOM full name | The permitted sources identify the licensee only as 'TPWODL' (and the website tpwesternodisha.com); the full registered name is not stated. | Pass 2: confirm full name and update the DISCOM field. | Resolved. 'TP Western Odisha Distribution Limited (TPWODL)' per the licence conditions, cl. 1.1 and 3.3(x) (S9). Main sheet updated. | TPWODL licence conditions (S9)
Drive links | Files were supplied without Google Drive URLs; the connected Google Drive was searched and holds no TPWODL or OERC documents. Link fields are recorded as not available. | Add Drive links when available. | Unchanged. Web sources are listed with their URLs in Source_Documentation; none has been uploaded to Drive.
Unit of voltage-case value | The HT value 1.5 reported for 'No. of cases ... exceeded 3% of the voltage limits' is fractional; S1, S2 and S3 give no unit or reporting instruction that explains it. | Pass 2: locate the licensee return or Commission reporting format. | Unresolved. No source explains a fractional HT value (1.5). The Guaranteed Standards report (S13) counts voltage complaints as whole numbers, a different measure. | Guaranteed Standards report FY 2022-23 (S13)
Scale of billing and meter shares | S3 reports faulty-bill and defective-meter shares as 0.0004 and 0.0013 under 'percentage' labels, far below the FY 2021-22 values (0.10 and 5); no licensee return explaining the change is in the repository. | Pass 2: check licensee returns. | Unresolved. The other licensees' values in the same S3 rows are of the order of 0.1 to 13, so TPWODL's 0.0004 and 0.0013 are outliers; no source explains the scale.
Draft amendment to the Standards of Performance Regulations (31 August 2019) | OERC notification no. OERC-Engg.-94/2003(Vol.-IV)/1251 proposing a '2nd Amendment'; the text says the Commission 'proposes' the amendments, with no sign of final notification. Not used as a standard. | Retrieve and review if a readable copy becomes available. | Recorded as an open item. | Draft 2nd Amendment, 2019 (excluded)
Draft Distribution Licensees' Standards of Performance Regulations, 2025 | Pre-published on 20 August 2025 for comments; draft, and later than FY 2022-23. Not used. | Retrieve and review if a readable copy becomes available. | Recorded as an open item. | Draft regulations, 2025 (excluded)
Overall Performance Standards page (licence Condition 17, 1997 licence) | Undated page on the OERC old site framed under the Orissa Electricity Reform Act, 1995 and the 1997 licence. Legal status and applicability to FY 2022-23 could not be established. Not used. | Retrieve and review if a readable copy becomes available. | Recorded as an open item. | OERC Overall Performance Standards page (not used)
TPWODL Standard Performance web page | Returned an access-denied response, so licensee-published standards of performance reports could not be read. | Retrieve and review if a readable copy becomes available. | Recorded as an open item. | TPWODL Standard Performance page (blocked)
Second copy of the FY 2022-23 Overall Standards statement | No public copy of the statement was located (a guessed file name on the licensee site returned an error page), so the TPWODL values rest on the supplied file only. | Retrieve and review if a readable copy becomes available. | Recorded as an open item. | OERC Performance of Discoms page
Existing Sources folder | A Drive folder named 'Sources' for this project could not be located with the available search (only an unrelated 'Source files' folder owned by another user was found), so its contents were not inspected and its completeness is not verified. | Retrieve and review if a readable copy becomes available. | Recorded as an open item.
Note on D2: Status updated after further review; see the linked evidence.
Note on E2: Evidence for the status in column D.
Note on D3: Status updated after further review; see the linked evidence.
Note on E3: Evidence for the status in column D.
Note on D4: Status updated after further review; see the linked evidence.
Note on E4: Evidence for the status in column D.
Note on D5: Status updated after further review; see the linked evidence.
Note on E5: Evidence for the status in column D.
Note on D6: Status updated after further review; see the linked evidence.
Note on E6: Evidence for the status in column D.
Note on D7: Status updated after further review; see the linked evidence.
Note on E7: Evidence for the status in column D.
Note on D8: Status updated after further review; see the linked evidence.
Note on E8: Evidence for the status in column D.
Note on D9: Status updated after further review; see the linked evidence.
Note on E9: Evidence for the status in column D.
Note on D10: Status updated after further review; see the linked evidence.
Note on E10: Evidence for the status in column D.
Note on D11: Status updated after further review; see the linked evidence.
Note on E11: Evidence for the status in column D.
Note on D12: Status updated after further review; see the linked evidence.
Note on E12: Evidence for the status in column D.
Note on D13: Status updated after further review; see the linked evidence.
Note on D14: Status updated after further review; see the linked evidence.
Note on E14: Evidence for the status in column D.
Note on D15: Status updated after further review; see the linked evidence.
Note on A16: New source-gap entry from the further review.
Note on E16: Link to the document or official hosting page concerned.
Note on A17: New source-gap entry from the further review.
Note on E17: Link to the document or official hosting page concerned.
Note on A18: New source-gap entry from the further review.
Note on E18: Link to the document or official hosting page concerned.
Note on A19: New source-gap entry from the further review.
Note on E19: Link to the document or official hosting page concerned.
Note on A20: New source-gap entry from the further review.
Note on E20: Link to the document or official hosting page concerned.
Note on A21: New source-gap entry from the further review.

## Data_Quality_Flags
Item | Observation | Treatment
Billing and meter shares | TPWODL reports faulty-bill share 0.0004 and defective-meter share 0.0013 under 'percentage' labels (FY 2021-22: 0.10 and 5). The values are far below last year's; the unit (per cent or fraction) is not stated beyond the label. In the same S3 rows the other licensees report 0.1, 1.49, 0.14 (bills) and 1.36, 13, 2.29 (meters); TPWODL's values are outliers. | Read as per cent and presented at source precision; compliance result is the same if read as fractions (0.04% and 0.13%); flagged.
Voltage HT value | HT value 1.5 under a 'No. of cases' label is fractional. EHT and LT show '--'. Other licensees in the same table show integer counts (0 for TPSODL). | Presented as published with unit not established; comparison marked not possible; flagged.
Voltage row wording | The FY 2022-23 row reads 'exceeded 3% of the voltage limits'; the FY 2021-22 row added 'fixed under I.E. Rules, 1956'. S1 sets voltage limits of +6/-6% (LV), +6/-9% (HV), +10/-12.5% (EHV) and a separate 3% voltage-unbalance limit. | Definitional mismatch recorded; no benchmark comparison made.
Scheduled-outage share | TPWODL reports 100.00 against a minimum target of 90 for 'completing the work within 12 hrs. of the scheduled outage before 5 PM/6 PM' (no value in FY 2021-22). S1 Sch. II 1.4 combines advance notice, a daily duration cap of 12 hours and restoration by 6 p.m. (summer) / 5 p.m. (winter). | Comparison marked not possible; see Review_Items.
Distribution-transformer shares | Urban 99.08% and rural 97.33% (FY 2021-22: both 100.00%). The S1 threshold applies to total DTs failed; case counts are not reported. | Compliance established because both area shares exceed 95%; combined share not derived.
S1 Sch. II 1.1 cross-reference | Sch. II 1.1 refers to the time limits in 'sub-paragraph 1.1 of Schedule-I', which concerns information on likely restoration time; the fuse-off time limits are in Sch. I 1.2. S3 applies the Sch. I 1.2 limits (6 / 24 hours). | Sch. I 1.2 time limits applied as the fuse-off time standard.
Line-breakdown clock start | S1 Sch. I 1.3 and Sch. II 1.2 measure time from occurrence of the breakdown; S3 measures 'within 12 hrs. / 24 hrs. of receiving the complaint'. | Comparison marked not possible; see Review_Items.
Billing-mistake wording | S1: 'bills requiring rectifications following complaints'; S3: 'faulty bills prepared'. Any bill requiring rectification after a complaint is a faulty bill, so the S3 share is not lower than the S1 share. | Treated as the same parameter; the 'met' result also holds under the narrower S1 definition.
Area terminology | S1 uses 'towns and cities' and 'rural areas'; S3 uses 'urban areas' and 'rural areas'; S2 defines Urban Areas as areas under NAC, Municipality and Municipal Corporation. | Treated as the same urban/rural classification.
Momentary-interruption threshold | S1 defines momentary as <= 5 minutes and sustained as > 5 minutes; S3 labels MAIFI 'less than 5 minutes' and SAIFI 'more than 5 minutes'. | Treated as the S1 definitions; interruptions of exactly 5 minutes may be classified inconsistently; flagged.
Reliability-index precision and weighting | SAIFI, MAIFI and SAIDI are reported as whole numbers and are weighted by connected load (kW), not by number of consumers. Footers and labels are unchanged from FY 2021-22. | Presented at source precision; unit stated per kW of connected load.
Large year-on-year changes | TPWODL SAIDI fell from 25,441 to 19,770 minutes, SAIFI from 600 to 468 and MAIFI from 66 to 40; accident cases: fatal animal 53 to 24, non-fatal human 16 to 24. | Reported as published; FY 2021-22 accident values in S3 agree with the FY 2021-22 statement (continuity check).
S3 document form | S3 is a single-page Commission statement with no issue date or reference number; accident counts are printed with leading zeros. | Recorded in Source_Documentation.
Note on B2: Cross-licensee comparison added from S3 (Calculations > Threshold_Tests).

## Review_Items
Item | Summary | Reason held for review
Line-breakdown comparability | S3 presents the share against the Commission's minimum target (95). The dashboard treats it as not comparable because the reported time is measured from receipt of complaint rather than from occurrence of the breakdown. | Methodological judgement; same treatment as FY 2021-22; confirm the licensee's measurement basis in Pass 2.
Scheduled-outage comparability | S3 reports 100.00 against a minimum target of 90. The dashboard treats it as not comparable because the standard also requires advance notice and a daily duration cap and the reported item is defined only by completion within 12 hours before 5 p.m. / 6 p.m. | Methodological judgement; first year with a reported value; confirm the licensee's definition in Pass 2.
Street-light rectification | No value reported for FY 2022-23 (FY 2021-22: reported value equal to the 90% target, treated as not comparable). | Revisit if Pass 2 locates a value and the licensee's measurement basis.
Aggregate vs area-level test (fuse-off, distribution transformer) | S1 sets a single aggregate threshold over total calls / DTs failed; S3 shows the target against each area. For FY 2022-23 both area shares are above the threshold for both parameters, so the aggregate test is passed under any weighting. | Method matters only where an area share falls below the threshold; record for other Odisha licensees.
CAIDI | Not specified in S1 and not reported in S3. | Not included in the main dataset.
Prior-year accident counts | S3 shows FY 2021-22 counts (FH 2, FA 53, NFH 16, NFA 0). S1 Sch. II 1.11 treats change over time as an indicator, without a target. | Held in Calculations > Accidents; continuity with the FY 2021-22 workbook confirmed.
Guaranteed Standards and compensation | Schedule I event-level standards and Schedule III compensation have no reported data for FY 2022-23 in the repository. | Source gap; add rows if Pass 2 locates data.
Overall Standards shares versus Guaranteed Standards counts | The FY 2022-23 Guaranteed Standards report (S13) lists case counts for TPWODL. On the reading obtained (column order not confirmable), the within-time proportions for urban and rural fuse-off calls are well below the 100.00% reported in the Overall Standards statement, and the transformer proportions are lower than 99.08% and 97.33%. The two documents may count different things (event-level limits, carry-over cases), and the dashboard rows continue to follow the Overall Standards statement. | Manual reading of S13 is needed before the fuse-off and distribution transformer compliance results are treated as settled.
Note on A9: Review item added from the newly located Guaranteed Standards report (S13).

## Conventions
Convention | Rule
Category convention | Supply-restoration and fault-rectification shares, billing mistakes and defective meters = Quality of Service; reliability indices, supply frequency and supply voltage = Quality & Reliability of Supply; accidents = Safety.
Indicator naming | '<Service> — share resolved within standard' for time-limited restoration parameters; '<Parameter> — <ratio>' for ratio standards; reliability indices use the full name with abbreviation; accidents follow 'Fatal / Non-fatal electrical accidents — humans / animals'.
Urban / rural | Where the standard and the reported data distinguish urban and rural areas, both appear in one row: area shares in Reported data; the combined FY share in the annualised field only where it can be derived without case counts (both area shares equal).
Percentages | One decimal place in the annualised field, e.g., 100.0%; Reported data retain source precision (e.g., 100.00%, 99.08%). Exception: where the reported value is below 0.1% (faulty-bill and defective-meter shares) the source precision is kept (0.0004%, 0.0013%) because one-decimal rounding would show 0.0%.
Indices | SAIDI in minutes, SAIFI in interruptions and MAIFI in momentary interruptions, each per kW of connected load (connected-load weighting per S1). Values are reported as annual whole numbers and are presented at source precision rather than two decimals.
FY notation | 'FY 2022-23' (April 2022 to March 2023).
Reported data | Final metric or concise series only, preserving the annual reporting basis and the urban/rural split; 'No value reported for FY 2022-23.' where the source shows '--'.
Annualised field | 'FY <metric>: <value>.'; 'Not annualised: no reported value.' where no value is reported; 'Not annualised: case counts required to combine the urban and rural shares are not reported.' where area shares differ and no counts are available.
Comparison rule | Comparison possible? = No ⇒ Standard met? = N/A, without exception. Yes only where definition, unit, period, area and aggregation level align; compliance assessed on the original regulatory basis (aggregate share over total cases).
Reference workbooks | TPWODL FY 2021-22 dashboard and calculations workbooks used as the primary template for format, naming, units, precision and structure; UGVCL FY 2024-25 workbooks as the wider dashboard reference. Neither used as evidence; all FY 2022-23 evidence re-established from the current sources.
DISCOM field | Registered name followed by the abbreviation in brackets, e.g., 'TP Western Odisha Distribution Limited (TPWODL)', as in the reference workbook.
Source IDs | Source IDs S5 to S13 follow the numbering used for FY 2021-22 where the same document is used; IDs not used in this year are omitted.
Note on B7: Corrected the dates in the FY notation convention (they showed April 2021 to March 2022); meaning of the notation unchanged.
Note on A12: Convention added with the DISCOM name update.
Note on A13: Convention added.