## Main
State | DISCOM | Financial year | Indicator category | Indicator | Standard | Reported data | Annualised / standardised reported data | Comparison possible? | Standard met? | If comparison is not possible, why? | Interpretation | Documentation of standardisation / transformation
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Intimation of charges (dedicated facility / extension / augmentation) — share resolved within standard (Urban) | 7 working days from application (Urban) | Within-standard share: Q1 75.2%; Q2 72.4%; Q3 70.7%; Q4 77.3%. | FY within-standard share: 74.0%. | No | N/A | The standard applies to the time taken for each individual request, complaint or event, while reported data are available only as an aggregate count of cases resolved within and beyond the standard; no aggregate performance threshold is specified. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Intimation of charges (dedicated facility / extension / augmentation) — share resolved within standard (Rural) | 10 working days (Rural); 15 working days (agricultural connections) | Within-standard share: Q1 47.6%; Q2 43.1%; Q3 47.2%; Q4 48.4%. | FY within-standard share: 46.7%. | No | N/A | The standard applies to the time taken for each individual request, complaint or event, while reported data are available only as an aggregate count of cases resolved within and beyond the standard; no aggregate performance threshold is specified. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | New connection / additional load from existing network — share resolved within standard | 7 days (Municipal Corporation in Metropolitan Area); 15 days (other Urban); 30 days (Rural), from completed application and payment | Within-standard share: Q1 42.1%; Q2 73.6%; Q3 65.7%; Q4 60.7%. | FY within-standard share: 59.3%. | No | N/A | The standard applies to the time taken for each individual request, complaint or event, while reported data are available only as an aggregate count of cases resolved within and beyond the standard; no aggregate performance threshold is specified. In addition, the standard differs by area (metropolitan, other urban, rural), while reported data are not split by area. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | New connection / additional load requiring extension / augmentation — share resolved within standard | 3 months from completed application and payment | Within-standard share: Q1 60.1%; Q2 72.2%; Q3 50.4%; Q4 38.6%. | FY within-standard share: 56.3%. | No | N/A | The standard applies to the time taken for each individual request, complaint or event, while reported data are available only as an aggregate count of cases resolved within and beyond the standard; no aggregate performance threshold is specified. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | New connection / additional load requiring new substation — share resolved within standard | 1 year from completed application and payment | No cases reported in any quarter. | Not annualised: no cases reported. | No | N/A | No cases were reported in any quarter, and the standard applies to the time taken for each individual case. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | None
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Shifting of meter / service line — share resolved within standard (Urban) | No quantitative time standard specified | Within-standard share: Q1 16.6%; Q2 29.4%; Q3 45.7%; Q4 43.0%. | FY within-standard share: 31.2%. | No | N/A | The applicable regulation does not specify a quantitative time standard for this service. | No quantitative regulatory benchmark is specified for direct comparison. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Shifting of meter / service line — share resolved within standard (Rural) | No quantitative time standard specified | Within-standard share: Q1 16.7%; Q2 46.8%; Q3 48.4%; Q4 46.2%. | FY within-standard share: 36.7%. | No | N/A | The applicable regulation does not specify a quantitative time standard for this service. | No quantitative regulatory benchmark is specified for direct comparison. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Reconnection of supply after payment of dues — share resolved within standard (Urban) | 8 hours from payment (Urban) | Within-standard share: Q1 5.0%; Q2 5.6%; Q3 6.1%; Q4 4.0%. | FY within-standard share: 4.9%. | No | N/A | The standard applies to the time taken for each individual request, complaint or event, while reported data are available only as an aggregate count of cases resolved within and beyond the standard; no aggregate performance threshold is specified. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Reconnection of supply after payment of dues — share resolved within standard (Rural) | 24 hours from payment (Rural) | Within-standard share: Q1 3.7%; Q2 6.5%; Q3 5.2%; Q4 4.0%. | FY within-standard share: 4.7%. | No | N/A | The standard applies to the time taken for each individual request, complaint or event, while reported data are available only as an aggregate count of cases resolved within and beyond the standard; no aggregate performance threshold is specified. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Change of name — share resolved within standard | By the second billing cycle from application | Within-standard share: Q1 83.6%; Q2 91.5%; Q3 87.2%; Q4 88.0%. | FY within-standard share: 88.3%. | No | N/A | The standard applies to the time taken for each individual request, complaint or event, while reported data are available only as an aggregate count of cases resolved within and beyond the standard; no aggregate performance threshold is specified. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Change of tariff category — share resolved within standard | By the second billing cycle from application | Within-standard share: Q1 82.5%; Q2 81.8%; Q3 82.4%; Q4 91.3%. | FY within-standard share: 86.0%. | No | N/A | The standard applies to the time taken for each individual request, complaint or event, while reported data are available only as an aggregate count of cases resolved within and beyond the standard; no aggregate performance threshold is specified. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Fuse-off call restoration — share resolved within standard (Urban) | 3 hours (Urban) | Within-standard share: Q1 26.1%; Q2 26.6%; Q3 26.6%; Q4 25.7%. | FY within-standard share: 26.3%. | No | N/A | The standard applies to the time taken for each individual request, complaint or event, while reported data are available only as an aggregate count of cases resolved within and beyond the standard; no aggregate performance threshold is specified. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Fuse-off call restoration — share resolved within standard (Rural) | 18 hours (Rural) | Within-standard share: Q1 45.4%; Q2 48.9%; Q3 43.4%; Q4 46.2%. | FY within-standard share: 46.2%. | No | N/A | The standard applies to the time taken for each individual request, complaint or event, while reported data are available only as an aggregate count of cases resolved within and beyond the standard; no aggregate performance threshold is specified. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Overhead line breakdown restoration — share resolved within standard (Urban) | 4 hours (Urban) | Within-standard share: Q1 12.3%; Q2 8.2%; Q3 12.1%; Q4 22.2%. | FY within-standard share: 12.2%. | No | N/A | The standard applies to the time taken for each individual request, complaint or event, while reported data are available only as an aggregate count of cases resolved within and beyond the standard; no aggregate performance threshold is specified. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Overhead line breakdown restoration — share resolved within standard (Rural) | 24 hours (Rural) | Within-standard share: Q1 36.5%; Q2 35.7%; Q3 34.9%; Q4 27.6%. | FY within-standard share: 34.4%. | No | N/A | The standard applies to the time taken for each individual request, complaint or event, while reported data are available only as an aggregate count of cases resolved within and beyond the standard; no aggregate performance threshold is specified. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Underground cable / bus-riser fault restoration — share resolved within standard (Urban) | 8 hours (Urban) | Within-standard share: Q1 14.4%; Q2 10.4%; Q3 14.1%; Q4 21.5%. | FY within-standard share: 14.1%. | No | N/A | The standard applies to the time taken for each individual request, complaint or event, while reported data are available only as an aggregate count of cases resolved within and beyond the standard; no aggregate performance threshold is specified. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Underground cable / bus-riser fault restoration — share resolved within standard (Rural) | 48 hours (Rural) | Within-standard share: Q1 42.4%; Q2 40.2%; Q3 35.2%; Q4 28.4%. | FY within-standard share: 36.9%. | No | N/A | The standard applies to the time taken for each individual request, complaint or event, while reported data are available only as an aggregate count of cases resolved within and beyond the standard; no aggregate performance threshold is specified. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Distribution transformer / switchgear failure restoration — share resolved within standard (Urban) | 18 hours (Urban) | Within-standard share: Q1 21.2%; Q2 17.9%; Q3 19.7%; Q4 22.7%. | FY within-standard share: 20.0%. | No | N/A | The standard applies to the time taken for each individual request, complaint or event, while reported data are available only as an aggregate count of cases resolved within and beyond the standard; no aggregate performance threshold is specified. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Distribution transformer / switchgear failure restoration — share resolved within standard (Rural) | 48 hours (Rural) | Within-standard share: Q1 28.8%; Q2 30.1%; Q3 27.8%; Q4 27.8%. | FY within-standard share: 28.7%. | No | N/A | The standard applies to the time taken for each individual request, complaint or event, while reported data are available only as an aggregate count of cases resolved within and beyond the standard; no aggregate performance threshold is specified. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Meter reading — share resolved within standard | Once every month (non-agricultural); once every three months (agricultural) | Within-standard share: Q1 81.0%; Q2 89.6%; Q3 90.0%; Q4 88.4%. | FY within-standard share: 87.3%. | No | N/A | The standard applies to the time taken for each individual request, complaint or event, while reported data are available only as an aggregate count of cases resolved within and beyond the standard; no aggregate performance threshold is specified. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Replacement of faulty meter — share resolved within standard (Urban) | Faulty meter replaced within the subsequent billing cycle | Within-standard share: Q1 62.4%; Q2 70.2%; Q3 71.1%; Q4 70.1%. | FY within-standard share: 67.6%. | No | N/A | The standard applies to the time taken for each individual request, complaint or event, while reported data are available only as an aggregate count of cases resolved within and beyond the standard; no aggregate performance threshold is specified. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Replacement of faulty meter — share resolved within standard (Rural) | Faulty meter replaced within the subsequent billing cycle | Within-standard share: Q1 45.2%; Q2 50.0%; Q3 66.1%; Q4 59.5%. | FY within-standard share: 52.6%. | No | N/A | The standard applies to the time taken for each individual request, complaint or event, while reported data are available only as an aggregate count of cases resolved within and beyond the standard; no aggregate performance threshold is specified. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Replacement of burnt meter — share resolved within standard (Urban) | 18 hours (Urban) | Within-standard share: Q1 15.0%; Q2 13.7%; Q3 14.6%; Q4 18.7%. | FY within-standard share: 15.1%. | No | N/A | The standard applies to the time taken for each individual request, complaint or event, while reported data are available only as an aggregate count of cases resolved within and beyond the standard; no aggregate performance threshold is specified. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Replacement of burnt meter — share resolved within standard (Rural) | 48 hours (Rural) | Within-standard share: Q1 21.5%; Q2 22.3%; Q3 22.3%; Q4 26.9%. | FY within-standard share: 23.0%. | No | N/A | The standard applies to the time taken for each individual request, complaint or event, while reported data are available only as an aggregate count of cases resolved within and beyond the standard; no aggregate performance threshold is specified. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Billing complaint resolution — share resolved within standard | Within 24 hours (non-receipt of bill / inadequate payment time); within the subsequent billing cycle (other billing complaints) | Within-standard share: Q1 77.9%; Q2 87.8%; Q3 89.9%; Q4 88.4%. | FY within-standard share: 86.4%. | No | N/A | The standard applies to the time taken for each individual request, complaint or event, while reported data are available only as an aggregate count of cases resolved within and beyond the standard; no aggregate performance threshold is specified. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Voltage-variation complaint resolution — share resolved within standard | No complaint-resolution time standard specified; supply-voltage limits are set in Regulation 22.5 (Tables 1–2) | Within-standard share: Q1 14.2%; Q2 12.9%; Q3 15.4%; Q4 19.8%. | FY within-standard share: 14.7%. | No | N/A | The applicable regulation does not specify a time standard for resolving voltage-variation complaints; the voltage limits it specifies cannot be compared with complaint-handling counts. | No quantitative regulatory benchmark is specified for direct comparison. | FY percentage calculated from annual numerator and denominator (cases resolved within standard ÷ total cases resolved, four non-overlapping quarters); quarterly percentages were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality of Service | Faulty meters rectified or replaced — share of faulty-meter stock | Faulty meter replaced within the subsequent billing cycle | Share of faulty meters rectified/replaced during quarter: Q1 9.4%; Q2 16.1%; Q3 20.9%; Q4 13.5%. | FY share rectified/replaced: 41.4%. | No | N/A | The standard applies to the replacement time of each individual faulty meter, while reported data are available only as quarterly stock and flow totals of faulty meters. | Direct comparison is not possible because the regulatory standard and reported performance use different measurement bases. | FY share calculated as meters rectified/replaced in the year ÷ (faulty meters at start of year + faulty meters added in the year); quarterly shares were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality & Reliability of Supply | System Average Interruption Duration Index (SAIDI) | No quantitative benchmark specified | Average monthly SAIDI (minutes per consumer): Q1 359.40; Q2 217.18; Q3 183.07; Q4 127.89. | FY SAIDI: 2,659.46 minutes per consumer. | No | N/A | No quantitative reliability benchmark applicable to FY 2021-22 is specified; the regulation requires efforts to achieve reliability standards fixed by the Commission from time to time. | No quantitative regulatory benchmark is specified for direct comparison. | Annual SAIDI reconstructed using the applicable formula (Σ ri×Ni ÷ Nt) from 12 monthly components, with Nt taken as the average monthly consumer count; quarterly values were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality & Reliability of Supply | System Average Interruption Frequency Index (SAIFI) | No quantitative benchmark specified | Average monthly SAIFI (interruptions per consumer): Q1 1.60; Q2 1.73; Q3 1.33; Q4 0.94. | FY SAIFI: 16.79 interruptions per consumer. | No | N/A | No quantitative reliability benchmark applicable to FY 2021-22 is specified; the regulation requires efforts to achieve reliability standards fixed by the Commission from time to time. | No quantitative regulatory benchmark is specified for direct comparison. | Annual SAIFI reconstructed using the applicable formula (Σ Ni ÷ Nt) from 12 monthly components, with Nt taken as the average monthly consumer count; quarterly values were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality & Reliability of Supply | Customer Average Interruption Duration Index (CAIDI) | No quantitative benchmark specified | CAIDI (minutes per interruption): Q1 225.16; Q2 125.43; Q3 137.44; Q4 136.21. | FY CAIDI: 158.37 minutes per interruption. | No | N/A | No quantitative reliability benchmark applicable to FY 2021-22 is specified; the regulation requires efforts to achieve reliability standards fixed by the Commission from time to time. | No quantitative regulatory benchmark is specified for direct comparison. | Annual CAIDI calculated as annual SAIDI ÷ annual SAIFI (equivalent to Σ ri×Ni ÷ Σ Ni over 12 months); quarterly values were not averaged.
Maharashtra | Maharashtra State Electricity Distribution Co. Ltd. (MSEDCL) | FY 2021-22 | Quality & Reliability of Supply | Customer Average Interruption Duration Index (CAIDI) — HT consumers | No quantitative benchmark specified | HT CAIDI (minutes per interruption): Q1 87.95; Q2 78.54; Q3 87.73; Q4 94.14. | FY HT CAIDI: 86.75 minutes per interruption. | No | N/A | No quantitative reliability benchmark applicable to FY 2021-22 is specified; the regulation requires efforts to achieve reliability standards fixed by the Commission from time to time. | No quantitative regulatory benchmark is specified for direct comparison. | Annual HT CAIDI calculated as Σ (ri×Ni) ÷ Σ Ni for HT consumers over 12 months; quarterly values were not averaged.

## Source_Documentation
ID | Source type | Source file name | Document title | Issuing authority | Publication / FY | Page(s) | Section / table / annexure | Google Drive link | Source note
S1 | Regulatory | MAHARASHTA REG 2021.pdf | MERC (Electricity Supply Code and Standards of Performance of Distribution Licensees including Power Quality) Regulations, 2021 | Maharashtra Electricity Regulatory Commission | Notified 2021 (No. MERC/Legal/2021/66); applicable throughout FY 2021-22 | pp.3, 8 (definitions); pp.51–52 (Reg. 22.12 reliability indices); p.55 (Reg. 24); p.59 (Reg. 27); pp.66–72 (Annexure II); pp.73–79 (Annexures III–VII) | Reg. 2.1, 22.12, 24, 27; Annexures II–VII | https://drive.google.com/file/d/13V5IpWC-hweTTiPBLWpNM1tMuRy7BTrI/view?usp=drivesdk | Applicable regulation: standards, definitions, units, formulas and reporting formats.
S2 | Regulatory | MAHARASHTRA 1ST AMEND 2024.pdf | Statement of Reasons — MERC Supply Code and SoP (First Amendment) Regulations, 2024 | Maharashtra Electricity Regulatory Commission | 5 July 2024 | pp.1–16 | Whole document | https://drive.google.com/file/d/1MWfvcn_lxDj3_5-i9T2Qpv55w_-a0oic/view?usp=drivesdk | Reviewed. Post-dates FY 2021-22 and is not applied. Amendments introduce CAIFI/MAIFI and revised connection timelines from 2024; confirms the 2021 Regulations were unamended before then (Introduction, p.1).
S3 | Reported performance | Quarter 1.pdf (MSEDCL / FY 2021-22 folder) | MSEDCL quarterly Standards of Performance return, Apr–Jun 2021 | MSEDCL (submitted to MERC) | FY 2021-22 | p.2 cover letter; p.3 Annex III; p.4 Annex IV; p.5 Annex V; p.6 Annex VI; p.7 Annex VII | Annexures III–VII | https://drive.google.com/file/d/11nt4CNutWqnXxotZOLPKNISeo9AFS6DY/view?usp=drivesdk | Reported quarterly performance. Field-office data, 'subject to subsequent corrections' per source note.
S4 | Reported performance | Quarter 2.pdf (MSEDCL / FY 2021-22 folder) | MSEDCL quarterly Standards of Performance return, Jul–Sep 2021 | MSEDCL (submitted to MERC) | FY 2021-22 | p.2 cover letter; p.3 Annex III; p.4 Annex IV; p.5 Annex V; p.6 Annex VI; p.7 Annex VII | Annexures III–VII | https://drive.google.com/file/d/1lZ8LuiZNzAOfEGcq7FJPaS3yQ8UEx9BG/view?usp=drivesdk | Reported quarterly performance. Field-office data, 'subject to subsequent corrections' per source note.
S5 | Reported performance | Quarter 3.pdf (MSEDCL / FY 2021-22 folder) | MSEDCL quarterly Standards of Performance return, Oct–Dec 2021 | MSEDCL (submitted to MERC) | FY 2021-22 | p.2 cover letter; p.3 Annex III; p.4 Annex IV; p.5 Annex V; p.6 Annex VI; p.7 Annex VII | Annexures III–VII | https://drive.google.com/file/d/1RB1lcK59SqHNkXO2q1YpCIE2FAvaT4uF/view?usp=drivesdk | Reported quarterly performance. Field-office data, 'subject to subsequent corrections' per source note.
S6 | Reported performance | Quarter 4.pdf (MSEDCL / FY 2021-22 folder) | MSEDCL quarterly Standards of Performance return, Jan–Mar 2022 | MSEDCL (submitted to MERC) | FY 2021-22 | p.2 cover letter; p.3 Annex III; p.4 Annex IV; p.5 Annex V; p.6 Annex VI; p.7 Annex VII | Annexures III–VII | https://drive.google.com/file/d/1QgBvjp4OjPkaCERH5pHOiYX-_VqXVFa6/view?usp=drivesdk | Reported quarterly performance. Field-office data, 'subject to subsequent corrections' per source note.

## Regulatory_Standards
Service / indicator | Area | Standard (original regulatory basis) | Source | Standard basis | Reporting format
Intimation of charges (dedicated facility / extension / augmentation) | Urban | 7 working days from application (Urban) | S1 — Annex II 1(i), p.66 | Event-level time standard | Annex III format, S1 p.73–75
Intimation of charges (dedicated facility / extension / augmentation) | Rural | 10 working days (Rural); 15 working days (agricultural connections) | S1 — Annex II 1(i), p.66 | Event-level time standard | Annex III format, S1 p.73–75
New connection / additional load from existing network | All | 7 days (Municipal Corporation in Metropolitan Area); 15 days (other Urban); 30 days (Rural), from completed application and payment | S1 — Annex II 1(ii), p.66 | Event-level time standard | Annex III format, S1 p.73–75
New connection / additional load requiring extension / augmentation | All | 3 months from completed application and payment | S1 — Annex II 1(ii), p.67 | Event-level time standard | Annex III format, S1 p.73–75
New connection / additional load requiring new substation | All | 1 year from completed application and payment | S1 — Annex II 1(ii), p.67 | Event-level time standard | Annex III format, S1 p.73–75
Shifting of meter / service line | Urban | No quantitative time standard specified | S1 — Annex II (not listed), p.66 | No quantitative time standard | Annex III format, S1 p.73–75
Shifting of meter / service line | Rural | No quantitative time standard specified | S1 — Annex II (not listed), p.66 | No quantitative time standard | Annex III format, S1 p.73–75
Reconnection of supply after payment of dues | Urban | 8 hours from payment (Urban) | S1 — Annex II 4, p.69 | Event-level time standard | Annex III format, S1 p.73–75
Reconnection of supply after payment of dues | Rural | 24 hours from payment (Rural) | S1 — Annex II 4, p.69 | Event-level time standard | Annex III format, S1 p.73–75
Change of name | All | By the second billing cycle from application | S1 — Annex II 7(ii), p.71 | Event-level time standard | Annex III format, S1 p.73–75
Change of tariff category | All | By the second billing cycle from application | S1 — Annex II 7(ii), p.71 | Event-level time standard | Annex III format, S1 p.73–75
Fuse-off call restoration | Urban | 3 hours (Urban) | S1 — Annex II 2(i), p.67 | Event-level time standard | Annex III format, S1 p.73–75
Fuse-off call restoration | Rural | 18 hours (Rural) | S1 — Annex II 2(i), p.67 | Event-level time standard | Annex III format, S1 p.73–75
Overhead line breakdown restoration | Urban | 4 hours (Urban) | S1 — Annex II 2(ii), p.67 | Event-level time standard | Annex III format, S1 p.73–75
Overhead line breakdown restoration | Rural | 24 hours (Rural) | S1 — Annex II 2(ii), p.67 | Event-level time standard | Annex III format, S1 p.73–75
Underground cable / bus-riser fault restoration | Urban | 8 hours (Urban) | S1 — Annex II 2(iii), p.67 | Event-level time standard | Annex III format, S1 p.73–75
Underground cable / bus-riser fault restoration | Rural | 48 hours (Rural) | S1 — Annex II 2(iii), p.67 | Event-level time standard | Annex III format, S1 p.73–75
Distribution transformer / switchgear failure restoration | Urban | 18 hours (Urban) | S1 — Annex II 2(iv), p.67 | Event-level time standard | Annex III format, S1 p.73–75
Distribution transformer / switchgear failure restoration | Rural | 48 hours (Rural) | S1 — Annex II 2(iv), p.67 | Event-level time standard | Annex III format, S1 p.73–75
Meter reading | All | Once every month (non-agricultural); once every three months (agricultural) | S1 — Annex II 7(i), p.70 | Event-level time standard | Annex III format, S1 p.73–75
Replacement of faulty meter | Urban | Faulty meter replaced within the subsequent billing cycle | S1 — Annex II 3(ii), p.68 | Event-level time standard | Annex III format, S1 p.73–75
Replacement of faulty meter | Rural | Faulty meter replaced within the subsequent billing cycle | S1 — Annex II 3(ii), p.68 | Event-level time standard | Annex III format, S1 p.73–75
Replacement of burnt meter | Urban | 18 hours (Urban) | S1 — Annex II 2(v), p.67 | Event-level time standard | Annex III format, S1 p.73–75
Replacement of burnt meter | Rural | 48 hours (Rural) | S1 — Annex II 2(v), p.67 | Event-level time standard | Annex III format, S1 p.73–75
Billing complaint resolution | All | Within 24 hours (non-receipt of bill / inadequate payment time); within the subsequent billing cycle (other billing complaints) | S1 — Annex II 5(ii), p.69 | Event-level time standard | Annex III format, S1 p.73–75
Voltage-variation complaint resolution | All | No complaint-resolution time standard specified; supply-voltage limits are set in Regulation 22.5 (Tables 1–2) | S1 — Annex II 8(i); Reg 22.5, p.71 | No quantitative time standard | Annex III format, S1 p.73–75
Faulty meter replacement | All | Within the subsequent billing cycle | S1 — Annex II 3(ii), p.68 | Event-level | Annex V format, S1 p.77
Meter inspection on complaint (not separately reported) | Urban / Rural | 4 days (Urban); 12 days (Rural) | S1 — Annex II 3(i), p.68 | Event-level | Not reported in Annexure III
SAIDI / SAIFI / CAIDI / HT CAIDI | All | No numeric benchmark; Reg. 22.12.4 refers to standards fixed by the Commission from time to time | S1 — Reg. 22.12.4, p.52 | None | Annex VII format, S1 p.79

## Definitions_Units
Indicator | Definition / formula | Dashboard unit | Reporting basis | Evidence | Note
Within-standard share (all Annexure III rows) | Cases resolved within the standard ÷ total cases resolved in the period (Annexure III columns f ÷ h) | Percentage (%) | Quarterly counts; FY from summed counts | Columns and formula h = f+g: S1 Annex III p.73; values S3–S6 p.3 | Classification 'within standard' is as reported by the licensee; the return does not show individual resolution times.
SAIDI | Average duration of sustained interruptions per consumer; SAIDI = Σ(ri×Ni) ÷ Nt | Minutes per consumer | Monthly; quarterly 'Total' row = monthly average | S1 Reg. 2.1(ddd) p.8 (minutes); Reg. 22.12.5 p.52; Annex VII p.79 | Excludes scheduled outages, interruptions ≤5 minutes, grid failures and force majeure (Reg. 22.12.1 proviso).
SAIFI | Average frequency of sustained interruptions per consumer; SAIFI = Σ Ni ÷ Nt | Interruptions per consumer (count ÷ count) | Monthly; quarterly 'Total' row = monthly average | S1 Reg. 2.1(eee) p.8; Reg. 22.12.5 p.52 | Unit derived from formula: number of consumer interruptions ÷ number of consumers.
CAIDI | Average duration per sustained interruption; CAIDI = SAIDI ÷ SAIFI | Minutes per interruption | Monthly / quarterly | S1 Reg. 2.1(j) p.3 (minutes); Reg. 22.12.5 p.52 | Minutes ÷ (interruptions per consumer) → minutes per interruption.
CAIDI — HT consumers | CAIDI computed only for HT consumers from their metering data | Minutes per interruption | Monthly / quarterly | S1 Reg. 22.12.5 proviso p.52; Annex VII table 4 p.79
Faulty-meter share rectified/replaced | Meters rectified/replaced ÷ total faulty meters (opening + added) | Percentage (%) | Quarterly stocks and flows | S1 Annex V p.77; values S3–S6 p.5 | Dashboard-derived ratio from reported stock/flow totals.

## Source_Gaps
Item | Gap (as of Pass 1) | Follow-up
Reliability benchmark | No numeric SAIDI/SAIFI/CAIDI benchmark applicable to FY 2021-22 was found in the permitted repository. Reg. 22.12.4 refers to standards 'fixed by the Commission from time to time'; any such order is not in the repository. | Pass 2: search MERC orders/directions on reliability targets for MSEDCL.
First Amendment regulation text | Only the Statement of Reasons (2024) is in the repository, not the notified amendment text. Not applicable to FY 2021-22. | Pass 2 (for later years): obtain notified amendment.
Any amendment/practice direction 2021–22 | No amendment, order or practice direction modifying Annexure II (Reg. 5.3 third proviso) during FY 2021-22 was found. | Pass 2: confirm none issued.
Annual Reg. 27.1 return | Annual SoP information (within 30 days of FY end) not found; quarterly returns used. | Pass 2: locate annual return.
Urban/rural reliability indices | Reg. 22.12.2 requires urban/rural data; returns report licensee-wide indices only. | Pass 2: locate disaggregated monthly website data.
Safety indicators | No safety standard or safety performance data (e.g., electrical accidents) found in the permitted repository for MSEDCL FY 2021-22. | Pass 2: search for accident statistics / Electrical Inspectorate data.
Power-quality parameters | Voltage, unbalance, dip/swell, harmonic standards exist (Reg. 22.5–22.11) but no measured performance was reported; compensation applicability for quality of supply was to be notified separately (Annex II note). | Pass 2: search for power-quality measurement reports.

## Data_Quality_Flags
Item | Observation | Treatment
Annex III row 3 (extension/augmentation), Q4 | Reported total complaints e = 180,845, but c+d = 179,845; reported closing pending 158,227 vs e−h = 157,227 (difference 1,000). | Shares use f and g only and are unaffected.
Annex III row 12 Rural, Q3 and Q4 | Q3 and Q4 Rural figures are identical in every column (330 / 1,517 / 1,847 / 400 / 1,041 / 1,441 / 406), and Q4 opening (330) ≠ Q3 closing (406). Possible repeated entry. | Values used as reported; flagged.
Annex III row 3, Q3 and Q4 | Complaints received in quarter identical (24,947) in Q3 and Q4. | Used as reported; flagged.
Annex III inter-quarter pending | Several parameters show closing pending ≠ next-quarter opening pending (see Calculations › AnnexIII_Recon), e.g., row 2: Q3 closing 328,486 vs Q4 opening 155,907. | Shares use within-quarter resolved counts only.
Annex V faulty meters, Q2 | Total 1,981,953 − rectified 318,328 = 1,663,625 vs reported closing 1,663,627 (difference 2). | Minor; flagged.
Annex VI agricultural meters, Q3→Q4 | Q3 end total 4,428,189 ≠ Q4 start 4,431,247. | Review item only.
Annex VII SAIDI numerator scope | Column 6 numerator labelled 'excluding agri. feeders' while Nt is total consumers. | Indices reproduced as reported; Pass 2 check.
Annex VII HT CAIDI columns | Column 4 ('Ri') equals column 5 ('Σ Ri×Ni') in every month. | Column 5 used, per source formula (5)/(3).
Annex IV, Q3 | Compensation amount for case 41 of 2019 truncated in source text layer. | Review item only.

## Review_Items
Item | Summary | Reason held for review
Compensation paid to consumers (Annexure IV) | Q1: 1 case (Ombudsman), Rs 22,758; Q2: nil; Q3: 1 case (CGRF), amount unclear; Q4: 2 cases (CGRF), Rs 3,850 | Not a performance standard; could map to Quality of Service or governance. Held for review.
Agricultural metering (Annexure VI) | Metered share of agricultural connections at end of quarter: Q1 65.8%; Q2 65.7%; Q3 65.6%; Q4 65.1% | Metering coverage does not clearly fall in the three dashboard categories; no quantitative standard. Held for review.
Voltage-variation complaint sub-types (17a–17c) | Within-standard shares by local fault / network / augmentation — see Calculations › AnnexIII_Source | Sub-components of the main-sheet voltage-complaint row; kept out of main sheet.

## Conventions
Convention | Rule
Category convention | Request/complaint handling times (Annex II/III, incl. supply-restoration complaints and voltage complaints) = Quality of Service; system-wide interruption indices = Quality & Reliability of Supply; Safety = accident/safety indicators.
Indicator naming | '<Service> — share resolved within standard (<Area>)'; area suffix only where the source splits Urban/Rural.
Percentages | One decimal place, e.g., 26.3%.
Indices | Two decimal places; SAIDI and CAIDI in minutes; SAIFI in interruptions per consumer.
FY notation | 'FY 2021-22' (April 2021 – March 2022); quarters Q1 = Apr–Jun … Q4 = Jan–Mar.
Reported data | Final metric series only, preserving the reporting basis (quarterly; monthly-average basis noted for indices).
Annualised field | 'FY <metric>: <value>.'
Comparison rule | Comparison possible? = No ⇒ Standard met? = N/A, without exception.