## MPCZ, MADHYA PRADESH
Madhya Pradesh Madhya Kshetra Vidyut Vitaran Company Limited
Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) Regulations, 2004 | Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) (Revision-II) Regulations, 2012 [No. RG-8 (II) of 2012] | Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) (Revision-II) (First Amendment) Regulations, 2012 {ARG-8 (II) (i) of 2021}.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Restoration of Power Supply | Normal Fuse of calls (Urban) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 4 hours on all working days and within 5 hours on all non-working days in urban areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Restoration of Power Supply | Normal Fuse of calls (Rural) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Restoration of Power Supply | Line Breakdown (Urban) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 12 daylight-hours in urban areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Restoration of Power Supply | Line Breakdown (Rural) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 3 days in rural areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Complaints about Meters | Meter Complaint (Urban) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 24 hours in urban areas . | 99.5 | % of cases to be resolved within specified time/standard. | 99.1 | % of cases resolved within specified time/standard | Yes | No | N/A
2021-22 | Complaints about Meters | Meter Complaint (Rural) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 72 hours in rural areas . | 98 | % of cases to be resolved within specified time/standard. | 98 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Urban) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 99.44 | % of cases resolved within specified time/standard | Yes | No | N/A
2021-22 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Rural) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 99.53 | % of cases resolved within specified time/standard | Yes | No | N/A
2021-22 | Transfer of Ownership and Conversion of service | Transfer of ownership and conversion of service | This refers to consumer title transfers, consumer category changes, or service phase conversions (LT single-phase to LT three-phase and vice-versa, or LT to HT and vice-versa) . | Within 15 days after completion of formalities. If line extension is required, it must be completed within 15 days from the payment of charges and submission of report and within 90 days . Time taken for change in consumer details must be within 10 days from the date of application . | 98 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Urban) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 4 hours of receipt of due payment from the consumer in towns and cities . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2021-22 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Rural) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 6 hours of receipt of due payment from the consumer in rural areas . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2021-22 | Consumer Bill Complaint | Billing Mistakes : Urban | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | 99.2 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Mistakes : Rural | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | 99 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Temporary Connections | Release of temporary connection (Urban) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Temporary Connections | Release of temporary connection (Rural) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | No Dues Certificate | Issuance of No dues certificate (Urban) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2021-22 | No Dues Certificate | Issuance of No dues certificate (Rural) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Power Supply | Period scheduled outage (Urban) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Restoration of Power Supply | Period scheduled outage (Rural) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Restoration of Power Supply | Normal Fuse of calls (Urban) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 4 hours on all working days and within 5 hours on all non-working days in urban areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Restoration of Power Supply | Normal Fuse of calls (Rural) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Restoration of Power Supply | Line Breakdown (Urban) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 12 daylight-hours in urban areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Restoration of Power Supply | Line Breakdown (Rural) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 3 days in rural areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Complaints about Meters | Meter Complaint (Urban) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 24 hours in urban areas . | 99.5 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Complaints about Meters | Meter Complaint (Rural) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 72 hours in rural areas . | 98 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Urban) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Rural) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Transfer of Ownership and Conversion of service | Transfer of ownership and conversion of service | This refers to consumer title transfers, consumer category changes, or service phase conversions (LT single-phase to LT three-phase and vice-versa, or LT to HT and vice-versa) . | Within 15 days after completion of formalities. If line extension is required, it must be completed within 15 days from the payment of charges and submission of report and within 90 days . Time taken for change in consumer details must be within 10 days from the date of application . | 98 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Urban) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 4 hours of receipt of due payment from the consumer in towns and cities . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2022-23 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Rural) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 6 hours of receipt of due payment from the consumer in rural areas . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2022-23 | Consumer Bill Complaint | Billing Mistakes : Urban | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Mistakes : Rural | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Temporary Connections | Release of temporary connection (Urban) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Temporary Connections | Release of temporary connection (Rural) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | No Dues Certificate | Issuance of No dues certificate (Urban) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2022-23 | No Dues Certificate | Issuance of No dues certificate (Rural) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Power Supply | Period scheduled outage (Urban) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Restoration of Power Supply | Period scheduled outage (Rural) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Restoration of Power Supply | Normal Fuse of calls (Urban) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 4 hours on all working days and within 5 hours on all non-working days in urban areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Restoration of Power Supply | Normal Fuse of calls (Rural) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Restoration of Power Supply | Line Breakdown (Urban) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 12 daylight-hours in urban areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Restoration of Power Supply | Line Breakdown (Rural) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 3 days in rural areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Complaints about Meters | Meter Complaint (Urban) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 24 hours in urban areas . | 99.5 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Complaints about Meters | Meter Complaint (Rural) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 72 hours in rural areas . | 98 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Urban) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Rural) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Transfer of Ownership and Conversion of service | Transfer of ownership and conversion of service | This refers to consumer title transfers, consumer category changes, or service phase conversions (LT single-phase to LT three-phase and vice-versa, or LT to HT and vice-versa) . | Within 15 days after completion of formalities. If line extension is required, it must be completed within 15 days from the payment of charges and submission of report and within 90 days . Time taken for change in consumer details must be within 10 days from the date of application . | 98 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Urban) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 4 hours of receipt of due payment from the consumer in towns and cities . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2023-24 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Rural) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 6 hours of receipt of due payment from the consumer in rural areas . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2023-24 | Consumer Bill Complaint | Billing Mistakes : Urban | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Consumer Bill Complaint | Billing Mistakes : Rural | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Temporary Connections | Release of temporary connection (Urban) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Temporary Connections | Release of temporary connection (Rural) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | No Dues Certificate | Issuance of No dues certificate (Urban) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2023-24 | No Dues Certificate | Issuance of No dues certificate (Rural) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Power Supply | Period scheduled outage (Urban) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Restoration of Power Supply | Period scheduled outage (Rural) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Restoration of Power Supply | Normal Fuse of calls (Urban) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 4 hours on all working days and within 5 hours on all non-working days in urban areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Normal Fuse of calls (Rural) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Line Breakdown (Urban) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 12 daylight-hours in urban areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Line Breakdown (Rural) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 3 days in rural areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Complaints about Meters | Meter Complaint (Urban) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 24 hours in urban areas . | 99.5 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Complaints about Meters | Meter Complaint (Rural) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 72 hours in rural areas . | 98 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Urban) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Rural) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Transfer of Ownership and Conversion of service | Transfer of ownership and conversion of service | This refers to consumer title transfers, consumer category changes, or service phase conversions (LT single-phase to LT three-phase and vice-versa, or LT to HT and vice-versa) . | Within 15 days after completion of formalities. If line extension is required, it must be completed within 15 days from the payment of charges and submission of report and within 90 days . Time taken for change in consumer details must be within 10 days from the date of application . | 98 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Urban) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 4 hours of receipt of due payment from the consumer in towns and cities . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Rural) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 6 hours of receipt of due payment from the consumer in rural areas . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Consumer Bill Complaint | Billing Mistakes : Urban | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Consumer Bill Complaint | Billing Mistakes : Rural | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Temporary Connections | Release of temporary connection (Urban) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Temporary Connections | Release of temporary connection (Rural) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | No Dues Certificate | Issuance of No dues certificate (Urban) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2024-25 | No Dues Certificate | Issuance of No dues certificate (Rural) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Period scheduled outage (Urban) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Period scheduled outage (Rural) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Restoration of Power Supply | Normal Fuse of calls (Urban) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 4 hours on all working days and within 5 hours on all non-working days in urban areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Normal Fuse of calls (Rural) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Line Breakdown (Urban) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 12 daylight-hours in urban areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Line Breakdown (Rural) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 3 days in rural areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Complaints about Meters | Meter Complaint (Urban) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 24 hours in urban areas . | 99.5 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Complaints about Meters | Meter Complaint (Rural) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 72 hours in rural areas . | 98 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Urban) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Rural) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Transfer of Ownership and Conversion of service | Transfer of ownership and conversion of service | This refers to consumer title transfers, consumer category changes, or service phase conversions (LT single-phase to LT three-phase and vice-versa, or LT to HT and vice-versa) . | Within 15 days after completion of formalities. If line extension is required, it must be completed within 15 days from the payment of charges and submission of report and within 90 days . Time taken for change in consumer details must be within 10 days from the date of application . | 98 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Urban) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 4 hours of receipt of due payment from the consumer in towns and cities . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Rural) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 6 hours of receipt of due payment from the consumer in rural areas . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Consumer Bill Complaint | Billing Mistakes : Urban | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Consumer Bill Complaint | Billing Mistakes : Rural | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Temporary Connections | Release of temporary connection (Urban) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Temporary Connections | Release of temporary connection (Rural) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | No Dues Certificate | Issuance of No dues certificate (Urban) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | No Dues Certificate | Issuance of No dues certificate (Rural) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Period scheduled outage (Urban) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Period scheduled outage (Rural) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.

## MPEZ,MADHYA PRADESH
Madhya Pradesh Poorva Kshetra Vidyut Vitaran Company Limited
Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) Regulations, 2004 | Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) (Revision-II) Regulations, 2012 [No. RG-8(II) of 2012] | Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) (Revision-II) (First Amendment) Regulations, 2012 {ARG-8 (II) (i) of 2021}.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Restoration of Power Supply | Normal Fuse of calls (Urban) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 4 hours on all working days and within 5 hours on all non-working days in urban areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Restoration of Power Supply | Normal Fuse of calls (Rural) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Restoration of Power Supply | Line Breakdown (Urban) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 12 daylight-hours in urban areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Restoration of Power Supply | Line Breakdown (Rural) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 3 days in rural areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Complaints about Meters | Meter Complaint (Urban) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 24 hours in urban areas . | 99.5 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Complaints about Meters | Meter Complaint (Rural) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 72 hours in rural areas . | 98 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Urban) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Rural) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Transfer of Ownership and Conversion of service | Transfer of ownership and conversion of service | This refers to consumer title transfers, consumer category changes, or service phase conversions (LT single-phase to LT three-phase and vice-versa, or LT to HT and vice-versa) . | Within 15 days after completion of formalities. If line extension is required, it must be completed within 15 days from the payment of charges and submission of report and within 90 days . Time taken for change in consumer details must be within 10 days from the date of application . | 98 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Urban) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 4 hours of receipt of due payment from the consumer in towns and cities . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2021-22 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Rural) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 6 hours of receipt of due payment from the consumer in rural areas . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2021-22 | Consumer Bill Complaint | Billing Mistakes : Urban | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Mistakes : Rural | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2021-22 | Temporary Connections | Release of temporary connection (Urban) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Temporary Connections | Release of temporary connection (Rural) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | No Dues Certificate | Issuance of No dues certificate (Urban) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2021-22 | No Dues Certificate | Issuance of No dues certificate (Rural) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Power Supply | Period scheduled outage (Urban) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | 93.34 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Restoration of Power Supply | Period scheduled outage (Rural) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | 95.06 | % of cases resolved within specified time/standard | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Restoration of Power Supply | Normal Fuse of calls (Urban) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 4 hours on all working days and within 5 hours on all non-working days in urban areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Restoration of Power Supply | Normal Fuse of calls (Rural) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Restoration of Power Supply | Line Breakdown (Urban) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 12 daylight-hours in urban areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Restoration of Power Supply | Line Breakdown (Rural) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 3 days in rural areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Complaints about Meters | Meter Complaint (Urban) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 24 hours in urban areas . | 99.5 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Complaints about Meters | Meter Complaint (Rural) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 72 hours in rural areas . | 98 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Urban) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Rural) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Transfer of Ownership and Conversion of service | Transfer of ownership and conversion of service | This refers to consumer title transfers, consumer category changes, or service phase conversions (LT single-phase to LT three-phase and vice-versa, or LT to HT and vice-versa) . | Within 15 days after completion of formalities. If line extension is required, it must be completed within 15 days from the payment of charges and submission of report and within 90 days . Time taken for change in consumer details must be within 10 days from the date of application . | 98 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Urban) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 4 hours of receipt of due payment from the consumer in towns and cities . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2022-23 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Rural) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 6 hours of receipt of due payment from the consumer in rural areas . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2022-23 | Consumer Bill Complaint | Billing Mistakes : Urban | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Mistakes : Rural | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Temporary Connections | Release of temporary connection (Urban) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Temporary Connections | Release of temporary connection (Rural) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | No Dues Certificate | Issuance of No dues certificate (Urban) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2022-23 | No Dues Certificate | Issuance of No dues certificate (Rural) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Power Supply | Period scheduled outage (Urban) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | 93.45 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Restoration of Power Supply | Period scheduled outage (Rural) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | 95.05 | % of cases resolved within specified time/standard | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Restoration of Power Supply | Normal Fuse of calls (Urban) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 4 hours on all working days and within 5 hours on all non-working days in urban areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Restoration of Power Supply | Normal Fuse of calls (Rural) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Restoration of Power Supply | Line Breakdown (Urban) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 12 daylight-hours in urban areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Restoration of Power Supply | Line Breakdown (Rural) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 3 days in rural areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Complaints about Meters | Meter Complaint (Urban) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 24 hours in urban areas . | 99.5 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Complaints about Meters | Meter Complaint (Rural) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 72 hours in rural areas . | 98 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Urban) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Rural) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Transfer of Ownership and Conversion of service | Transfer of ownership and conversion of service | This refers to consumer title transfers, consumer category changes, or service phase conversions (LT single-phase to LT three-phase and vice-versa, or LT to HT and vice-versa) . | Within 15 days after completion of formalities. If line extension is required, it must be completed within 15 days from the payment of charges and submission of report and within 90 days . Time taken for change in consumer details must be within 10 days from the date of application . | 98 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Urban) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 4 hours of receipt of due payment from the consumer in towns and cities . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2023-24 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Rural) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 6 hours of receipt of due payment from the consumer in rural areas . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2023-24 | Consumer Bill Complaint | Billing Mistakes : Urban | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | 90.94 | % of cases resolved within specified time/standard | Yes | No | N/A
2023-24 | Consumer Bill Complaint | Billing Mistakes : Rural | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | 87.26 | % of cases resolved within specified time/standard | Yes | No | N/A
2023-24 | Temporary Connections | Release of temporary connection (Urban) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Temporary Connections | Release of temporary connection (Rural) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | No Dues Certificate | Issuance of No dues certificate (Urban) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2023-24 | No Dues Certificate | Issuance of No dues certificate (Rural) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Power Supply | Period scheduled outage (Urban) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | 98.02 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Restoration of Power Supply | Period scheduled outage (Rural) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | 97.36 | % of cases resolved within specified time/standard | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Restoration of Power Supply | Normal Fuse of calls (Urban) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 4 hours on all working days and within 5 hours on all non-working days in urban areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Normal Fuse of calls (Rural) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Line Breakdown (Urban) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 12 daylight-hours in urban areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Line Breakdown (Rural) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 3 days in rural areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Complaints about Meters | Meter Complaint (Urban) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 24 hours in urban areas . | 99.5 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Complaints about Meters | Meter Complaint (Rural) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 72 hours in rural areas . | 98 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Urban) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Rural) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Transfer of Ownership and Conversion of service | Transfer of ownership and conversion of service | This refers to consumer title transfers, consumer category changes, or service phase conversions (LT single-phase to LT three-phase and vice-versa, or LT to HT and vice-versa) . | Within 15 days after completion of formalities. If line extension is required, it must be completed within 15 days from the payment of charges and submission of report and within 90 days . Time taken for change in consumer details must be within 10 days from the date of application . | 98 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Urban) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 4 hours of receipt of due payment from the consumer in towns and cities . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Rural) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 6 hours of receipt of due payment from the consumer in rural areas . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Consumer Bill Complaint | Billing Mistakes : Urban | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Mistakes : Rural | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Temporary Connections | Release of temporary connection (Urban) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Temporary Connections | Release of temporary connection (Rural) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | No Dues Certificate | Issuance of No dues certificate (Urban) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2024-25 | No Dues Certificate | Issuance of No dues certificate (Rural) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Period scheduled outage (Urban) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Period scheduled outage (Rural) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Restoration of Power Supply | Normal Fuse of calls (Urban) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 4 hours on all working days and within 5 hours on all non-working days in urban areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Normal Fuse of calls (Rural) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Line Breakdown (Urban) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 12 daylight-hours in urban areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Line Breakdown (Rural) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 3 days in rural areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Complaints about Meters | Meter Complaint (Urban) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 24 hours in urban areas . | 99.5 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Complaints about Meters | Meter Complaint (Rural) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 72 hours in rural areas . | 98 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Urban) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Rural) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Transfer of Ownership and Conversion of service | Transfer of ownership and conversion of service | This refers to consumer title transfers, consumer category changes, or service phase conversions (LT single-phase to LT three-phase and vice-versa, or LT to HT and vice-versa) . | Within 15 days after completion of formalities. If line extension is required, it must be completed within 15 days from the payment of charges and submission of report and within 90 days . Time taken for change in consumer details must be within 10 days from the date of application . | 98 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Urban) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 4 hours of receipt of due payment from the consumer in towns and cities . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Rural) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 6 hours of receipt of due payment from the consumer in rural areas . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Consumer Bill Complaint | Billing Mistakes : Urban | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Mistakes : Rural | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Temporary Connections | Release of temporary connection (Urban) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Temporary Connections | Release of temporary connection (Rural) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | No Dues Certificate | Issuance of No dues certificate (Urban) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | No Dues Certificate | Issuance of No dues certificate (Rural) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Period scheduled outage (Urban) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Period scheduled outage (Rural) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.

## MPWZ,MADHYA PRADESH
Madhya Pradesh Paschim Kshetra Vidyut Vitaran Company Limited
Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) Regulations, 2004 | Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) (Revision-II) Regulations, 2012 [No. RG-8(II) of 2012] | Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) (Revision-II) (First Amendment) Regulations, 2012 {ARG-8 (II) (i) of 2021}.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard | Benchmark meaning | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Restoration of Power Supply | Normal Fuse of calls (Urban) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 4 hours on all working days and within 5 hours on all non-working days in urban areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Restoration of Power Supply | Normal Fuse of calls (Rural) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Restoration of Power Supply | Line Breakdown (Urban) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 12 daylight-hours in urban areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Restoration of Power Supply | Line Breakdown (Rural) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 3 days in rural areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Complaints about Meters | Meter Complaint (Urban) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 24 hours in urban areas . | 99.5 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Complaints about Meters | Meter Complaint (Rural) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 72 hours in rural areas . | 98 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Urban) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Rural) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Transfer of Ownership and Conversion of service | Transfer of ownership and conversion of service | This refers to consumer title transfers, consumer category changes, or service phase conversions (LT single-phase to LT three-phase and vice-versa, or LT to HT and vice-versa) . | Within 15 days after completion of formalities. If line extension is required, it must be completed within 15 days from the payment of charges and submission of report and within 90 days . Time taken for change in consumer details must be within 10 days from the date of application . | 98 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Urban) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 4 hours of receipt of due payment from the consumer in towns and cities . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2021-22 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Rural) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 6 hours of receipt of due payment from the consumer in rural areas . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2021-22 | Consumer Bill Complaint | Billing Mistakes : Urban | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Mistakes : Rural | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Temporary Connections | Release of temporary connection (Urban) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Temporary Connections | Release of temporary connection (Rural) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | No Dues Certificate | Issuance of No dues certificate (Urban) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2021-22 | No Dues Certificate | Issuance of No dues certificate (Rural) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Power Supply | Period scheduled outage (Urban) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Restoration of Power Supply | Period scheduled outage (Rural) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Restoration of Power Supply | Normal Fuse of calls (Urban) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 4 hours on all working days and within 5 hours on all non-working days in urban areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Restoration of Power Supply | Normal Fuse of calls (Rural) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Restoration of Power Supply | Line Breakdown (Urban) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 12 daylight-hours in urban areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Restoration of Power Supply | Line Breakdown (Rural) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 3 days in rural areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Complaints about Meters | Meter Complaint (Urban) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 24 hours in urban areas . | 99.5 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Complaints about Meters | Meter Complaint (Rural) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 72 hours in rural areas . | 98 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Urban) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Rural) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Transfer of Ownership and Conversion of service | Transfer of ownership and conversion of service | This refers to consumer title transfers, consumer category changes, or service phase conversions (LT single-phase to LT three-phase and vice-versa, or LT to HT and vice-versa) . | Within 15 days after completion of formalities. If line extension is required, it must be completed within 15 days from the payment of charges and submission of report and within 90 days . Time taken for change in consumer details must be within 10 days from the date of application . | 98 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Urban) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 4 hours of receipt of due payment from the consumer in towns and cities . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2022-23 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Rural) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 6 hours of receipt of due payment from the consumer in rural areas . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2022-23 | Consumer Bill Complaint | Billing Mistakes : Urban | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Mistakes : Rural | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Temporary Connections | Release of temporary connection (Urban) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Temporary Connections | Release of temporary connection (Rural) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | No Dues Certificate | Issuance of No dues certificate (Urban) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2022-23 | No Dues Certificate | Issuance of No dues certificate (Rural) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Power Supply | Period scheduled outage (Urban) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Restoration of Power Supply | Period scheduled outage (Rural) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Restoration of Power Supply | Normal Fuse of calls (Urban) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 4 hours on all working days and within 5 hours on all non-working days in urban areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Restoration of Power Supply | Normal Fuse of calls (Rural) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Restoration of Power Supply | Line Breakdown (Urban) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 12 daylight-hours in urban areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Restoration of Power Supply | Line Breakdown (Rural) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 3 days in rural areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Complaints about Meters | Meter Complaint (Urban) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 24 hours in urban areas . | 99.5 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Complaints about Meters | Meter Complaint (Rural) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 72 hours in rural areas . | 98 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Urban) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Rural) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Transfer of Ownership and Conversion of service | Transfer of ownership and conversion of service | This refers to consumer title transfers, consumer category changes, or service phase conversions (LT single-phase to LT three-phase and vice-versa, or LT to HT and vice-versa) . | Within 15 days after completion of formalities. If line extension is required, it must be completed within 15 days from the payment of charges and submission of report and within 90 days . Time taken for change in consumer details must be within 10 days from the date of application . | 98 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Urban) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 4 hours of receipt of due payment from the consumer in towns and cities . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2023-24 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Rural) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 6 hours of receipt of due payment from the consumer in rural areas . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2023-24 | Consumer Bill Complaint | Billing Mistakes : Urban | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Consumer Bill Complaint | Billing Mistakes : Rural | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Temporary Connections | Release of temporary connection (Urban) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Temporary Connections | Release of temporary connection (Rural) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | No Dues Certificate | Issuance of No dues certificate (Urban) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2023-24 | No Dues Certificate | Issuance of No dues certificate (Rural) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Power Supply | Period scheduled outage (Urban) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Restoration of Power Supply | Period scheduled outage (Rural) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Restoration of Power Supply | Normal Fuse of calls (Urban) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 4 hours on all working days and within 5 hours on all non-working days in urban areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Normal Fuse of calls (Rural) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Line Breakdown (Urban) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 12 daylight-hours in urban areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Line Breakdown (Rural) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 3 days in rural areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Complaints about Meters | Meter Complaint (Urban) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 24 hours in urban areas . | 99.5 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Complaints about Meters | Meter Complaint (Rural) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 72 hours in rural areas . | 98 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Urban) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Rural) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Transfer of Ownership and Conversion of service | Transfer of ownership and conversion of service | This refers to consumer title transfers, consumer category changes, or service phase conversions (LT single-phase to LT three-phase and vice-versa, or LT to HT and vice-versa) . | Within 15 days after completion of formalities. If line extension is required, it must be completed within 15 days from the payment of charges and submission of report and within 90 days . Time taken for change in consumer details must be within 10 days from the date of application . | 98 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Urban) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 4 hours of receipt of due payment from the consumer in towns and cities . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Rural) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 6 hours of receipt of due payment from the consumer in rural areas . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Consumer Bill Complaint | Billing Mistakes : Urban | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Mistakes : Rural | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Temporary Connections | Release of temporary connection (Urban) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Temporary Connections | Release of temporary connection (Rural) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | No Dues Certificate | Issuance of No dues certificate (Urban) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2024-25 | No Dues Certificate | Issuance of No dues certificate (Rural) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Period scheduled outage (Urban) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Period scheduled outage (Rural) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Restoration of Power Supply | Normal Fuse of calls (Urban) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 4 hours on all working days and within 5 hours on all non-working days in urban areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Normal Fuse of calls (Rural) | Normal Fuse-off Call involves restoring power supply by replacing Horn Gap (HG) or Low Tension (LT) fuses at the distribution transformer or at the consumer's premises . | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Line Breakdown (Urban) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 12 daylight-hours in urban areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Line Breakdown (Rural) | Line Breakdown refers to restoring electricity supply after overhead line faults or line breakdowns, excluding cases where poles are broken or uprooted . | The distribution licensee must restore power supply following line breakdowns within 3 days in rural areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Complaints about Meters | Meter Complaint (Urban) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 24 hours in urban areas . | 99.5 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Complaints about Meters | Meter Complaint (Rural) | Meter Complaint refers to consumer complaints regarding the inspection, checking of correctness, or replacement of slow, creeping, stuck-up, or burnt meters . | The distribution licensee must inspect and check meter correctness within 7 days . Defective (slow, creeping, stuck-up) or burnt meters must be replaced within 72 hours in rural areas . | 98 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Urban) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Application for New Connection or Additional Load | Application for new connection/ additional load / reduction of load (Rural) | This refers to processing applications and releasing new LT, HT, or EHT electricity connections, or executing contract demand enhancement or reduction . | The distribution licensee must process applications and release connections within the timeframes as notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Transfer of Ownership and Conversion of service | Transfer of ownership and conversion of service | This refers to consumer title transfers, consumer category changes, or service phase conversions (LT single-phase to LT three-phase and vice-versa, or LT to HT and vice-versa) . | Within 15 days after completion of formalities. If line extension is required, it must be completed within 15 days from the payment of charges and submission of report and within 90 days . Time taken for change in consumer details must be within 10 days from the date of application . | 98 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Urban) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 4 hours of receipt of due payment from the consumer in towns and cities . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Reconnection of Supply following Disconnection | Reconnection of supply following disconnection (Rural) | This refers to restoring the electricity supply of a consumer whose connection was cut off for non-payment of bills, following receipt of payment . | The distribution licensee must reconnect the consumer's supply within 6 hours of receipt of due payment from the consumer in rural areas . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Consumer Bill Complaint | Billing Mistakes : Urban | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Mistakes : Rural | Bills requiring modifications following complaints | % of bills requiring modifications following complaints to the total number of bills issued, at a value not greater than 1%. | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Temporary Connections | Release of temporary connection (Urban) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Temporary Connections | Release of temporary connection (Rural) | Release of temporary connection refers to providing short-term electricity connections for construction, festivals, or private/public events as per the Supply Code . | The distribution licensee must release temporary connections for LT, HT, and EHT consumers within the timelines specified and notified under the Electricity Supply Code as applicable . | 100 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | No Dues Certificate | Issuance of No dues certificate (Urban) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | No Dues Certificate | Issuance of No dues certificate (Rural) | This refers to the issuing of a clearance certificate confirming no outstanding dues remain on a consumer's account upon permanent disconnection or premises vacation . | The distribution licensee must issue a no dues certificate upon receiving final payment in case of vacation of premises or permanent disconnections, as specified in the Supply Code as applicable . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Period scheduled outage (Urban) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Period scheduled outage (Rural) | Period scheduled outage refers to planned, pre-notified power interruptions carried out by the distribution licensee for maintenance work on the network, which must not exceed 4 times a year . | The distribution licensee must ensure that planned scheduled outages do not exceed 12 hours in a single stretch, and supply must be restored by 6:00 PM (with exceptions reported if delayed past 6:00 PM up to 8:00 PM) . | 90 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available.

## MSEDCL, MAHARASHTRA
Maharashtra State Electricity Distribution Company Limited
Maharashtra Electricity Regulatory Commission (Electricity Supply Code and Standards of Performance of Distribution Licensees including Power Quality) Regulations, 2021 (upto to 4th July 2024) | Maharashtra Electricity Regulatory Commission (Electricity Supply Code and Standards of Performance of Distribution Licensees including Power Quality) (First Amendment) Regulations, 2024. (starts 5th July 2024)
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Provision of Supply | Intimation of charges where supply to dedicated or after extension / augmentation (Urban) | The estimated expenses an applicant has to pay after submitting an application for a dedicated distribution facility or network extension | Charges must be intimated within seven (7) working days in Urban Areas. | N/A | N/A | 54.59 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Provision of Supply | Intimation of charges where supply to dedicated or after extension / augmentation (Rural) | The estimated expenses an applicant has to pay after submitting an application for a dedicated distribution facility or network extension | Charges must be intimated within ten (10) working days in Rural Areas. | N/A | N/A | 30.3 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Provision of Supply | New connection / add. Load where supply from existing line. | Release of a new connection or modification of an existing connection where electricity supply is provided from the existing network without requiring any line extension or capacity expansion | 7 days for Municipal Corporation within Metropolitan Area, 15 days for other urban areas, and 30 days for rural areas | N/A | N/A | 32.04 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Provision of Supply | New connection / add. Load where supply after extension / augmentation. | Provision of electricity supply to an applicant where an extension or capacity upgrade of the distribution main network is required to service the request | Supply must be provided within 3 months. | N/A | N/A | 7.97 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Provision of Supply | New connection / add. Load where supply after commissioning of sub-station. | Provision of electricity supply to an applicant where the project requires commissioning a brand-new distribution substation as part of the licensee's grid. | 1 Year | N/A | N/A | N/A | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Shifting of Services | Shifting of Meter / service line (Urban) | Shifting of a consumer's meter or service line to another position or location within the premises in Urban Areas. | Shifting must be completed within the second billing cycle. |  | N/A | 15.9 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Shifting of Services | Shifting of Meter / service line (Rural) | Shifting of a consumer's meter or service line to another position or location within the premises in Rural Areas. | Shifting must be completed within the second billing cycle. | N/A | N/A | 11.51 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Reconnection | Reconnection of supply after payment of dues (Urban) | Reconnection of a Consumer who has been disconnected for less than six (6) months, from the time of payment of outstanding amounts or payment under protest. | Reconnection must be completed within eight (8) hours in Urban Areas. | N/A | N/A | 3.25 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Reconnection | Reconnection of supply after payment of dues (Rural) | Reconnection of a Consumer who has been disconnected for less than six (6) months, from the time of payment of outstanding amounts or payment under protest. | Reconnection must be completed within twenty-four (24) hours in Rural Areas. | N/A | N/A | 3.02 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Other Services | Change of Name | Transfer of a connection in the name of another person upon application. | Name change must be completed within the second billing cycle. | N/A | N/A | 63.6 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Other Services | Change of category | Classification or reclassification of a Consumer into various approved tariff categories based on the purpose of usage of supply. | Change of category must be completed within the second billing cycle. | N/A | N/A | 64.12 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Fuse off call (Urban) | Complaint handling involving restoration of supply by replacement of a fuse at an individual Consumer's premises, not simultaneous with other failures. | Supply must be restored within three (3) hours in Urban Areas. | N/A | N/A | 25.28 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Fuse off call (Rural) | Complaint handling involving restoration of supply by replacement of a fuse at an individual Consumer's premises, not simultaneous with other failures. | Supply must be restored within eighteen (18) hours in Rural Areas. | N/A | N/A | 43.02 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Break down of Over head Line (Urban) | Restoration of supply following a breakdown on 33kV/ 22kV/ 11kV/400 V overhead lines. | Supply must be restored within four (4) hours in Urban Areas. | N/A | N/A | 11.03 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Break down of Over head Line (Rural) | Restoration of supply following a breakdown on 33kV/ 22kV/ 11kV/400 V overhead lines. | Supply must be restored within twenty-four (24) hours in Rural Areas. | N/A | N/A | 29.41 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Underground Cable fault / Bus Riser Fault (Urban) | Restoration of supply following an underground cable fault or a Bus Riser fault in the network. | Supply must be restored within eight (8) hours in Urban Areas. | N/A | N/A | 12.02 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Underground Cable fault / Bus Riser Fault (Rural) | Restoration of supply following an underground cable fault or a Bus Riser fault in the network. | Supply must be restored within forty-eight (48) hours in Rural Areas. | N/A | N/A | 22.48 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Transformer and Associated Switchgear Failure (Urban) | Restoration of supply following the failure of a distribution transformer and its associated switchgear. | Supply must be restored within eighteen (18) hours in Urban Areas. | N/A | N/A | 18.29 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Transformer and Associated Switchgear Failure (Rural) | Restoration of supply following the failure of a distribution transformer and its associated switchgear. | Supply must be restored within forty-eight (48) hours in Rural Areas. | N/A | N/A | 23.16 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Other Services | Meter Reading | Reading of the consumer's meter manually, via meter reading instrument, or through AMR. | Meters must be read once in every three months for agricultural Consumers and every month for all other Consumers. | N/A | N/A | 72.81 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Replacement of Faulty Meter (Urban) | Inspection and replacement of an electricity meter if it is found to be faulty/defective. | Replacement must be completed within the subsequent billing cycle. | N/A | N/A | 44.82 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Replacement of Faulty Meter (Rural) | Inspection and replacement of an electricity meter if it is found to be faulty/defective. | Replacement must be completed within the subsequent billing cycle. | N/A | N/A | 23.03 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Replacement of Burnt Meter (Urban) | Replacement of a meter and restoration of supply where the meter is found to be burnt. | Restoration and replacement must be completed within eighteen (18) hours in Urban Areas. | N/A | N/A | 10.11 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Replacement of Burnt Meter (Rural) | Replacement of a meter and restoration of supply where the meter is found to be burnt. | Restoration and replacement must be completed within forty-eight (48) hours in Rural Areas. | N/A | N/A | 9.4 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations. | Annual Performance (Formula 1)
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Provision of Supply | Intimation of charges where supply to dedicated or after extension / augmentation (Urban) | The estimated expenses an applicant has to pay after submitting an application for a dedicated distribution facility or network extension | Charges must be intimated within seven (7) working days in Urban Areas. | N/A | N/A | 61.98% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2022-23 | Provision of Supply | Intimation of charges where supply to dedicated or after extension / augmentation (Rural) | The estimated expenses an applicant has to pay after submitting an application for a dedicated distribution facility or network extension | Charges must be intimated within ten (10) working days in Rural Areas. | N/A | N/A | 35.32% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2022-23 | Provision of Supply | New connection / add. Load where supply from existing line. | Release of a new connection or modification of an existing connection where electricity supply is provided from the existing network without requiring any line extension or capacity expansion | 7 days for Municipal Corporation within Metropolitan Area, 15 days for other urban areas, and 30 days for rural areas | N/A | N/A | 26.85% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2022-23 | Provision of Supply | New connection / add. Load where supply after extension / augmentation. | Provision of electricity supply to an applicant where an extension or capacity upgrade of the distribution main network is required to service the request | Supply must be provided within 3 months. | N/A | N/A | 3.98% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2022-23 | Provision of Supply | New connection / add. Load where supply after commissioning of sub-station. | Provision of electricity supply to an applicant where the project requires commissioning a brand-new distribution substation as part of the licensee's grid. | Supply must be provided within 1 year. | N/A | N/A | -- | No Cases | No | N/A | No benchmark defined in regulations.
2022-23 | Shifting of Services | Shifting of Meter / service line (Urban) | Shifting of a consumer's meter or service line to another position or location within the premises in Urban Areas. | Shifting must be completed within the second billing cycle. | N/A | N/A | 20.28% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2022-23 | Shifting of Services | Shifting of Meter / service line (Rural) | Shifting of a consumer's meter or service line to another position or location within the premises in Rural Areas. | Shifting must be completed within the second billing cycle. | N/A | N/A | 8.92% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2022-23 | Reconnection | Reconnection of supply after payment of dues (Urban) | Reconnection of a Consumer who has been disconnected for less than six (6) months, from the time of payment of outstanding amounts or payment under protest. | Reconnection must be completed within eight (8) hours in Urban Areas. | N/A | N/A | 2.16% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2022-23 | Reconnection | Reconnection of supply after payment of dues (Rural) | Reconnection of a Consumer who has been disconnected for less than six (6) months, from the time of payment of outstanding amounts or payment under protest. | Reconnection must be completed within twenty-four (24) hours in Rural Areas. | N/A | N/A | 2.03% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2022-23 | Other Services | Change of Name | Transfer of a connection in the name of another person upon application. | Name change must be completed within the second billing cycle. | N/A | N/A | 66.31% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2022-23 | Other Services | Change of category | Classification or reclassification of a Consumer into various approved tariff categories based on the purpose of usage of supply. | Change of category must be completed within the second billing cycle. | N/A | N/A | 59.85% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Fuse off call (Urban) | Complaint handling involving restoration of supply by replacement of a fuse at an individual Consumer's premises, not simultaneous with other failures. | Supply must be restored within three (3) hours in Urban Areas. | N/A | N/A | 21.18% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Fuse off call (Rural) | Complaint handling involving restoration of supply by replacement of a fuse at an individual Consumer's premises, not simultaneous with other failures. | Supply must be restored within eighteen (18) hours in Rural Areas. | N/A | N/A | 34.67% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Break down of Over head Line (Urban) | Restoration of supply following a breakdown on 33kV/ 22kV/ 11kV/400 V overhead lines. | Supply must be restored within four (4) hours in Urban Areas. | N/A | N/A | 19.74% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Break down of Over head Line (Rural) | Restoration of supply following a breakdown on 33kV/ 22kV/ 11kV/400 V overhead lines. | Supply must be restored within twenty-four (24) hours in Rural Areas. | N/A | N/A | 23.81% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Underground Cable fault / Bus Riser Fault (Urban) | Restoration of supply following an underground cable fault or a Bus Riser fault in the network. | Supply must be restored within eight (8) hours in Urban Areas. | N/A | N/A | 13.77% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Underground Cable fault / Bus Riser Fault (Rural) | Restoration of supply following an underground cable fault or a Bus Riser fault in the network. | Supply must be restored within forty-eight (48) hours in Rural Areas. | N/A | N/A | 15.42% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Transformer and Associated Switchgear Failure (Urban) | Restoration of supply following the failure of a distribution transformer and its associated switchgear. | Supply must be restored within eighteen (18) hours in Urban Areas. | N/A | N/A | 20.83% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Transformer and Associated Switchgear Failure (Rural) | Restoration of supply following the failure of a distribution transformer and its associated switchgear. | Supply must be restored within forty-eight (48) hours in Rural Areas. | N/A | N/A | 18.74% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2022-23 | Other Services | Meter Reading | Reading of the consumer's meter manually, via meter reading instrument, or through AMR. | Meters must be read once in every three months for agricultural Consumers and every month for all other Consumers. | N/A | N/A | 59.59% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Replacement of Faulty Meter (Urban) | Inspection and replacement of an electricity meter if it is found to be faulty/defective. | Replacement must be completed within the subsequent billing cycle. | N/A | N/A | 31.44% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Replacement of Faulty Meter (Rural) | Inspection and replacement of an electricity meter if it is found to be faulty/defective. | Replacement must be completed within the subsequent billing cycle. | N/A | N/A | 16% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Replacement of Burnt Meter (Urban) | Replacement of a meter and restoration of supply where the meter is found to be burnt. | Restoration and replacement must be completed within eighteen (18) hours in Urban Areas. | N/A | N/A | 7.81% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Replacement of Burnt Meter (Rural) | Replacement of a meter and restoration of supply where the meter is found to be burnt. | Restoration and replacement must be completed within forty-eight (48) hours in Rural Areas. | N/A | N/A | 6.74% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Provision of Supply | Intimation of charges where supply to dedicated or after extension / augmentation (Urban) | The estimated expenses an applicant has to pay after submitting an application for a dedicated distribution facility or network extension | Charges must be intimated within seven (7) working days in Urban Areas. | N/A | N/A | 97.83% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Provision of Supply | Intimation of charges where supply to dedicated or after extension / augmentation (Rural) | The estimated expenses an applicant has to pay after submitting an application for a dedicated distribution facility or network extension | Charges must be intimated within ten (10) working days in Rural Areas. | N/A | N/A | 68.98% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Provision of Supply | New connection / add. Load where supply from existing line. | Release of a new connection or modification of an existing connection where electricity supply is provided from the existing network without requiring any line extension or capacity expansion | 7 days for Municipal Corporation within Metropolitan Area, 15 days for other urban areas, and 30 days for rural areas | N/A | N/A | 48.86% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Provision of Supply | New connection / add. Load where supply after extension / augmentation. | Provision of electricity supply to an applicant where an extension or capacity upgrade of the distribution main network is required to service the request | Supply must be provided within 3 months. | N/A | N/A | 9.93% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Provision of Supply | New connection / add. Load where supply after commissioning of sub-station. | Provision of electricity supply to an applicant where the project requires commissioning a brand-new distribution substation as part of the licensee's grid. | Supply must be provided within 1 year. | N/A | N/A | 4.4% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Shifting of Services | Shifting of Meter / service line (Urban) | Shifting of a consumer's meter or service line to another position or location within the premises in Urban Areas. | Shifting must be completed within the second billing cycle. | N/A | N/A | 62.02% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Shifting of Services | Shifting of Meter / service line (Rural) | Shifting of a consumer's meter or service line to another position or location within the premises in Rural Areas. | Shifting must be completed within the second billing cycle. | N/A | N/A | 52.8% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Reconnection | Reconnection of supply after payment of dues (Urban) | Reconnection of a Consumer who has been disconnected for less than six (6) months, from the time of payment of outstanding amounts or payment under protest. | Reconnection must be completed within eight (8) hours in Urban Areas. | N/A | N/A | 4.53% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Reconnection | Reconnection of supply after payment of dues (Rural) | Reconnection of a Consumer who has been disconnected for less than six (6) months, from the time of payment of outstanding amounts or payment under protest. | Reconnection must be completed within twenty-four (24) hours in Rural Areas. | N/A | N/A | 2.79% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Other Services | Change of Name | Transfer of a connection in the name of another person upon application. | Name change must be completed within the second billing cycle. | N/A | N/A | 74.85% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Other Services | Change of category | Classification or reclassification of a Consumer into various approved tariff categories based on the purpose of usage of supply. | Change of category must be completed within the second billing cycle. | N/A | N/A | 60.03% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Fuse off call (Urban) | Complaint handling involving restoration of supply by replacement of a fuse at an individual Consumer's premises, not simultaneous with other failures. | Supply must be restored within three (3) hours in Urban Areas. | N/A | N/A | 62.93% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Fuse off call (Rural) | Complaint handling involving restoration of supply by replacement of a fuse at an individual Consumer's premises, not simultaneous with other failures. | Supply must be restored within eighteen (18) hours in Rural Areas. | N/A | N/A | 77.72% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Break down of Over head Line (Urban) | Restoration of supply following a breakdown on 33kV/ 22kV/ 11kV/400 V overhead lines. | Supply must be restored within four (4) hours in Urban Areas. | N/A | N/A | 61.37% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Break down of Over head Line (Rural) | Restoration of supply following a breakdown on 33kV/ 22kV/ 11kV/400 V overhead lines. | Supply must be restored within twenty-four (24) hours in Rural Areas. | N/A | N/A | 71.21% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Underground Cable fault / Bus Riser Fault (Urban) | Restoration of supply following an underground cable fault or a Bus Riser fault in the network. | Supply must be restored within eight (8) hours in Urban Areas. | N/A | N/A | 59.55% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Underground Cable fault / Bus Riser Fault (Rural) | Restoration of supply following an underground cable fault or a Bus Riser fault in the network. | Supply must be restored within forty-eight (48) hours in Rural Areas. | N/A | N/A | 68.46% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Transformer and Associated Switchgear Failure (Urban) | Restoration of supply following the failure of a distribution transformer and its associated switchgear. | Supply must be restored within eighteen (18) hours in Urban Areas. | N/A | N/A | 55.62% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Transformer and Associated Switchgear Failure (Rural) | Restoration of supply following the failure of a distribution transformer and its associated switchgear. | Supply must be restored within forty-eight (48) hours in Rural Areas. | N/A | N/A | 60.71% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Other Services | Meter Reading | Reading of the consumer's meter manually, via meter reading instrument, or through AMR. | Meters must be read once in every three months for agricultural Consumers and every month for all other Consumers. | N/A | N/A | 86.21% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Replacement of Faulty Meter (Urban) | Inspection and replacement of an electricity meter if it is found to be faulty/defective. | Replacement must be completed within the subsequent billing cycle. | N/A | N/A | 62.03% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Replacement of Faulty Meter (Rural) | Inspection and replacement of an electricity meter if it is found to be faulty/defective. | Replacement must be completed within the subsequent billing cycle. | N/A | N/A | 46.67% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Replacement of Burnt Meter (Urban) | Replacement of a meter and restoration of supply where the meter is found to be burnt. | Restoration and replacement must be completed within eighteen (18) hours in Urban Areas. | N/A | N/A | 66.67% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Replacement of Burnt Meter (Rural) | Replacement of a meter and restoration of supply where the meter is found to be burnt. | Restoration and replacement must be completed within forty-eight (48) hours in Rural Areas. | N/A | N/A | 66.18% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Provision of Supply | Intimation of charges where supply to dedicated or after extension / augmentation (Urban) | The estimated expenses an applicant has to pay after submitting an application for a dedicated distribution facility or network extension | Charges must be intimated within seven (7) working days in Urban Areas. | N/A | N/A | 98.39% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Provision of Supply | Intimation of charges where supply to dedicated or after extension / augmentation (Rural) | The estimated expenses an applicant has to pay after submitting an application for a dedicated distribution facility or network extension | Charges must be intimated within ten (10) working days in Rural Areas. | N/A | N/A | 83.67% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Provision of Supply | New connection / add. Load where supply from existing line. | Release of a new connection or modification of an existing connection where electricity supply is provided from the existing network without requiring any line extension or capacity expansion | 1 Apr-4 Jul 2024 = old standards: Supply must be provided within seven (7) days in Metropolitan Areas, fifteen (15) days in other Municipal Areas, and thirty (30) days in Rural Areas. from 5 Jul 2024 = amended standards: Supply must be provided within three (3) days in Metropolitan Areas, seven (7) days in other Municipal Areas, and fifteen (15) days in Rural Areas. | N/A | N/A | 76.03% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Provision of Supply | New connection / add. Load where supply after extension / augmentation. | Provision of electricity supply to an applicant where an extension or capacity upgrade of the distribution main network is required to service the request | 1 Apr-4 Jul 2024 = old standards: Supply must be provided within 3 months. 5 Jul 2024 = amended standards: Supply must be provided within ninety (90) days. | N/A | N/A | 21.57% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Provision of Supply | New connection / add. Load where supply after commissioning of sub-station. | Provision of electricity supply to an applicant where the project requires commissioning a brand-new distribution substation as part of the licensee's grid. | 1 Apr-4 Jul 2024 = old standards: Supply must be provided within 1 year. 5 Jul 2024 = amended standards: Supply must be provided within ninety (90) days. | N/A | N/A | 0.68% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Shifting of Services | Shifting of Meter / service line (Urban) | Shifting of a consumer's meter or service line to another position or location within the premises in Urban Areas. | Shifting must be completed within the second billing cycle. | N/A | N/A | 47.44% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Shifting of Services | Shifting of Meter / service line (Rural) | Shifting of a consumer's meter or service line to another position or location within the premises in Rural Areas. | Shifting must be completed within the second billing cycle. | N/A | N/A | 48.57% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Reconnection | Reconnection of supply after payment of dues (Urban) | Reconnection of a Consumer who has been disconnected for less than six (6) months, from the time of payment of outstanding amounts or payment under protest. | Reconnection must be completed within eight (8) hours in Urban Areas. | N/A | N/A | 4.67% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Reconnection | Reconnection of supply after payment of dues (Rural) | Reconnection of a Consumer who has been disconnected for less than six (6) months, from the time of payment of outstanding amounts or payment under protest. | Reconnection must be completed within twenty-four (24) hours in Rural Areas. | N/A | N/A | 3.65% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Other Services | Change of Name | Transfer of a connection in the name of another person upon application. | Name change must be completed within the second billing cycle. | N/A | N/A | 87.69% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Other Services | Change of category | Classification or reclassification of a Consumer into various approved tariff categories based on the purpose of usage of supply. | Change of category must be completed within the second billing cycle. | N/A | N/A | 64.21% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | Fuse off call (Urban) | Complaint handling involving restoration of supply by replacement of a fuse at an individual Consumer's premises, not simultaneous with other failures. | Supply must be restored within three (3) hours in Urban Areas. | N/A | N/A | 79.44% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | Fuse off call (Rural) | Complaint handling involving restoration of supply by replacement of a fuse at an individual Consumer's premises, not simultaneous with other failures. | Supply must be restored within eighteen (18) hours in Rural Areas. | N/A | N/A | 92.82% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | Break down of Over head Line (Urban) | Restoration of supply following a breakdown on 33kV/ 22kV/ 11kV/400 V overhead lines. | Supply must be restored within four (4) hours in Urban Areas. | N/A | N/A | 74.05% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | Break down of Over head Line (Rural) | Restoration of supply following a breakdown on 33kV/ 22kV/ 11kV/400 V overhead lines. | Supply must be restored within twenty-four (24) hours in Rural Areas. | N/A | N/A | 83.8% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | Underground Cable fault / Bus Riser Fault (Urban) | Restoration of supply following an underground cable fault or a Bus Riser fault in the network. | Supply must be restored within eight (8) hours in Urban Areas. | N/A | N/A | 78.78% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | Underground Cable fault / Bus Riser Fault (Rural) | Restoration of supply following an underground cable fault or a Bus Riser fault in the network. | Supply must be restored within forty-eight (48) hours in Rural Areas. | N/A | N/A | 90.94% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | Transformer and Associated Switchgear Failure (Urban) | Restoration of supply following the failure of a distribution transformer and its associated switchgear. | Supply must be restored within eighteen (18) hours in Urban Areas. | N/A | N/A | 50.55% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | Transformer and Associated Switchgear Failure (Rural) | Restoration of supply following the failure of a distribution transformer and its associated switchgear. | Supply must be restored within forty-eight (48) hours in Rural Areas. | N/A | N/A | 60.15% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Other Services | Meter Reading | Reading of the consumer's meter manually, via meter reading instrument, or through AMR. | Meters must be read once in every three months for agricultural Consumers and every month for all other Consumers. | N/A | N/A | 97.55% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | Replacement of Faulty Meter (Urban) | Inspection and replacement of an electricity meter if it is found to be faulty/defective. | Replacement must be completed within the subsequent billing cycle. | N/A | N/A | 97.47% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | Replacement of Faulty Meter (Rural) | Inspection and replacement of an electricity meter if it is found to be faulty/defective. | Replacement must be completed within the subsequent billing cycle. | N/A | N/A | 95.87% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | Replacement of Burnt Meter (Urban) | Replacement of a meter and restoration of supply where the meter is found to be burnt. | Restoration and replacement must be completed within eighteen (18) hours in Urban Areas. | N/A | N/A | 69.66% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | Replacement of Burnt Meter (Rural) | Replacement of a meter and restoration of supply where the meter is found to be burnt. | Restoration and replacement must be completed within forty-eight (48) hours in Rural Areas. | N/A | N/A | 74.67% | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Provision of Supply | Intimation of charges where supply to dedicated or after extension / augmentation (Urban) | The estimated expenses an applicant has to pay after submitting an application for a dedicated distribution facility or network extension | Charges must be intimated within seven (7) working days in Urban Areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Provision of Supply | Intimation of charges where supply to dedicated or after extension / augmentation (Rural) | The estimated expenses an applicant has to pay after submitting an application for a dedicated distribution facility or network extension | Charges must be intimated within ten (10) working days in Rural Areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Provision of Supply | New connection / add. Load where supply from existing line. | Release of a new connection or modification of an existing connection where electricity supply is provided from the existing network without requiring any line extension or capacity expansion | Supply must be provided within three (3) days in Metropolitan Areas, seven (7) days in other Municipal Areas, and fifteen (15) days in Rural Areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Provision of Supply | New connection / add. Load where supply after extension / augmentation. | Provision of electricity supply to an applicant where an extension or capacity upgrade of the distribution main network is required to service the request | Supply must be provided within ninety (90) days. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Provision of Supply | New connection / add. Load where supply after commissioning of sub-station. | Provision of electricity supply to an applicant where the project requires commissioning a brand-new distribution substation as part of the licensee's grid. | Supply must be provided within ninety (90) days. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Shifting of Services | Shifting of Meter / service line (Urban) | Shifting of a consumer's meter or service line to another position or location within the premises in Urban Areas. | Shifting must be completed within the second billing cycle. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Shifting of Services | Shifting of Meter / service line (Rural) | Shifting of a consumer's meter or service line to another position or location within the premises in Rural Areas. | Shifting must be completed within the second billing cycle. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Reconnection | Reconnection of supply after payment of dues (Urban) | Reconnection of a Consumer who has been disconnected for less than six (6) months, from the time of payment of outstanding amounts or payment under protest. | Reconnection must be completed within eight (8) hours in Urban Areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Reconnection | Reconnection of supply after payment of dues (Rural) | Reconnection of a Consumer who has been disconnected for less than six (6) months, from the time of payment of outstanding amounts or payment under protest. | Reconnection must be completed within twenty-four (24) hours in Rural Areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Other Services | Change of Name | Transfer of a connection in the name of another person upon application. | Name change must be completed within the second billing cycle. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Other Services | Change of category | Classification or reclassification of a Consumer into various approved tariff categories based on the purpose of usage of supply. | Change of category must be completed within the second billing cycle. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Fuse off call (Urban) | Complaint handling involving restoration of supply by replacement of a fuse at an individual Consumer's premises, not simultaneous with other failures. | Supply must be restored within three (3) hours in Urban Areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Fuse off call (Rural) | Complaint handling involving restoration of supply by replacement of a fuse at an individual Consumer's premises, not simultaneous with other failures. | Supply must be restored within eighteen (18) hours in Rural Areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Break down of Over head Line (Urban) | Restoration of supply following a breakdown on 33kV/ 22kV/ 11kV/400 V overhead lines. | Supply must be restored within four (4) hours in Urban Areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Break down of Over head Line (Rural) | Restoration of supply following a breakdown on 33kV/ 22kV/ 11kV/400 V overhead lines. | Supply must be restored within twenty-four (24) hours in Rural Areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Underground Cable fault / Bus Riser Fault (Urban) | Restoration of supply following an underground cable fault or a Bus Riser fault in the network. | Supply must be restored within eight (8) hours in Urban Areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Underground Cable fault / Bus Riser Fault (Rural) | Restoration of supply following an underground cable fault or a Bus Riser fault in the network. | Supply must be restored within forty-eight (48) hours in Rural Areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Transformer and Associated Switchgear Failure (Urban) | Restoration of supply following the failure of a distribution transformer and its associated switchgear. | Supply must be restored within eighteen (18) hours in Urban Areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Transformer and Associated Switchgear Failure (Rural) | Restoration of supply following the failure of a distribution transformer and its associated switchgear. | Supply must be restored within forty-eight (48) hours in Rural Areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Other Services | Meter Reading | Reading of the consumer's meter manually, via meter reading instrument, or through AMR. | Meters must be read once in every three months for agricultural Consumers and every month for all other Consumers. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Replacement of Faulty Meter (Urban) | Inspection and replacement of an electricity meter if it is found to be faulty/defective. | Replacement must be completed within the subsequent billing cycle. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Replacement of Faulty Meter (Rural) | Inspection and replacement of an electricity meter if it is found to be faulty/defective. | Replacement must be completed within the subsequent billing cycle. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Replacement of Burnt Meter (Urban) | Replacement of a meter and restoration of supply where the meter is found to be burnt. | Restoration and replacement must be completed within eighteen (18) hours in Urban Areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Replacement of Burnt Meter (Rural) | Replacement of a meter and restoration of supply where the meter is found to be burnt. | Restoration and replacement must be completed within forty-eight (48) hours in Rural Areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.

## Calculations for MSEDCL
Financial Year | Period / Quarter | SAIDI Numerator (ΣRi*Ni) | SAIFI Numerator (ΣNi) | Total Customers (Nt) | HT Duration Numerator (ΣRi*Ni_HT) | HT Interrupted Customers (ΣNi_HT)
FY 2023-24 | Q1 (June 2023 Quarter) | 8,51,07,35,056 | 8,71,48,407 | 7,42,42,951 | 1,65,67,161 | 1,90,645
FY 2023-24 | Q2 (September 2023 Quarter) | 9,19,12,46,981 | 10,63,86,156 | 7,52,90,965 | 1,44,78,952 | 1,83,520
FY 2023-24 | Q3 (December 2023 Quarter) | 7,14,38,16,575 | 7,54,39,720 | 7,60,97,556 | 1,46,14,932 | 1,58,558
FY 2023-24 | Q4 (March 2024 Quarter) | 7,00,77,82,250 | 7,15,73,223 | 7,66,21,892 | 1,41,39,451 | 1,48,315
FY 2023-24 Total | Sum of Quarters
Financial Year | Period / Quarter | SAIDI Numerator (ΣRi*Ni) | SAIFI Numerator (ΣNi) | Total Customers (Nt) | HT Duration Numerator (ΣRi*Ni_HT) | HT Interrupted Customers (ΣNi_HT)
FY 2024-25 | Q1 (June 2024 Quarter) | 9,81,67,60,201 | 9,32,68,610 | 7,70,41,958 | 1,73,58,263 | 2,13,743
FY 2024-25 | Q2 (September 2024 Quarter) | 13,39,47,03,922 | 31,34,97,435 | 7,78,54,836 | 1,60,84,305 | 2,11,144
FY 2024-25 Total | Sum of Q1 & Q2
Financial Year | Period / Quarter | SAIDI Numerator (ΣRi*Ni) | SAIFI Numerator (ΣNi) | Total Customers (Nt) | HT Duration Numerator (ΣRi*Ni_HT) | HT Interrupted Customers (ΣNi_HT)
FY 2025-26 | Q1 (June 2025 Quarter) | 14,06,23,01,544 | 27,17,62,628 | 7,91,53,352 | 1,65,87,774 | 2,08,359
FY 2025-26 | Q2 (September 2025 Quarter) | 11,03,03,54,348 | 20,28,75,290 | 8,00,46,683 | 1,41,72,636 | 1,73,384
FY 2025-26 | October 2025 Month | 2,83,28,25,154 | 5,37,18,549 | 2,68,69,832 | - | -
FY 2025-26 | November 2025 Month | 4,37,24,56,436 | 7,60,05,941 | 2,69,59,652 | - | -
FY 2025-26 | December 2025 Month | 3,74,42,65,585 | 6,96,03,855 | 2,70,41,134 | - | -
FY 2025-26 | January 2026 Month | 3,09,22,33,419 | 5,42,89,984 | 2,70,93,187 | - | -
FY 2025-26 | February 2026 Month | 2,81,55,60,337 | 3,87,68,555 | 2,71,42,825 | - | -
FY 2025-26 | March 2026 Month | 4,04,72,33,501 | 4,77,18,076 | 2,72,29,896 | - | -
FY 2025-26 Total | Sum of Months/Quarters
Annual SAIDI (System Average Interruption Duration Index) | Sum of Quarterly Durations / Sum of Customer Bases | Σ(Ri * Ni) / ΣNt
Annual SAIFI (System Average Interruption Frequency Index) | Sum of Quarterly Interruptions / Sum of Customer Bases | ΣNi / ΣNt
Annual CAIDI (Customer Average Interruption Duration Index) | Annual SAIDI / Annual SAIFI | SAIDI_Annual / SAIFI_Annual
Annual CAIDI HT (CAIDI for High Tension Consumers) | Sum of HT Interruption Durations / Sum of HT Interrupted Customers | Σ(Ri * Ni)_HT / ΣNi_HT
$$\text{Annual Performance (\%)} = \left( \frac{\sum \text{Complaints Redressed in Time (Q1 to Q4)}}{\sum \text{Total Complaints (Q1 to Q4)}} \right) \times 100$$

## TGSPDCL, TELANGANA
Southern Power Distribution Company of Telangana Limited
Telangana State Electricity Regulatory Commission (Licensees’ Standards of Performance) Regulation, 2016.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Restoration of Supply | Normal Fuse-Off Calls | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | Cities & towns: 4 working hours; Rural: 8 working hours | 99 | % of calls rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2021-22 | Restoration of Supply | Line Breakdowns | Restoration of power supply following an overhead line/cable breakdown. | Cities & towns: 6 hours; Rural: 24 hours | 95 | % of cases resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2021-22 | Scheduled Outage | Scheduled Outage: Maximum Duration in a Single Stretch | Duration of a scheduled power interruption, excluding load-shedding, which must not exceed the prescribed maximum duration. | Maximum 12 hours in a day | 95 | % of cases complying with the specified maximum-duration standard | 100 | % of cases complying with the specified maximum-duration standard | Yes | Yes | N/A
2021-22 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Supply restored by 6:00 PM | 95 | % of cases in which supply was restored within the specified time | 100 | % of cases in which supply was restored within the specified time | Yes | Yes | N/A
2021-22 | Street Light Faults | Street Light Faults: Rectification of Line Faults | Rectification of line faults and restoration of streetlights. | Within 24 hours of detection or receipt of complaint, whichever is earlier | 90 | % of cases resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2021-22 | Street Light Faults | Street Light Faults: Replacement of Fused/Defective Unit | Replacement of a fused light or rectification/replacement of a defective street-light unit where the licensee is responsible for maintenance. | Within 24 hours of detection or receipt of complaint, whichever is earlier | 90 | % of cases resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2021-22 | Billing Performance | % Billing Mistakes | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | 0.1 | Maximum permissible % of bills requiring modification following complaints | 100 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
2021-22 | Metering Performance | % Faulty Meters | Percentage of defective meters relative to the total number of meters in service. | N/A | 3 | Maximum permissible % of defective meters among meters in service | 100 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
2021-22 | Power Supply Quality | Frequency Variation | Variation in the frequency of the electricity supply from its prescribed frequency, | To maintain supply frequency within 49.0 Hz to 50.5 Hz | N/A | N/A | 100 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
2021-22 | Power Supply Quality | Voltage Unbalance | Difference or imbalance in voltage at the point of commencement of supply, | Must not exceed 3% at the point of commencement of supply | N/A | N/A | 100 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why? | S.No. | Service Indicator | Annual Total Complaints (C) | Annual Total Redressed on Time | Calculated Annual OSoP %
2022-23 | Restoration of Supply | Normal Fuse-Off Calls | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | Cities & towns: 4 working hours; Rural: 8 working hours | 99 | % of calls rectified within the specified time limits | 90.92 | % of calls rectified within the specified time limits | Yes | No | N/A | 1 | Normal Fuse-Off Calls | 655888 | 596357 | 90.92%
2022-23 | Restoration of Supply | Line Breakdowns | Restoration of power supply following an overhead line/cable breakdown. | Cities & towns: 6 hours; Rural: 24 hours | 95 | % of cases resolved within the specified time limit | 76.29 | % of cases resolved within the specified time limit | Yes | No | N/A | 2 | Line Breakdowns | 22792 | 17389 | 76.29%
2022-23 | Scheduled Outage | Scheduled Outage: Maximum Duration in a Single Stretch | Duration of a scheduled power interruption, excluding load-shedding, which must not exceed the prescribed maximum duration. | Maximum 12 hours in a day | 95 | % of cases complying with the specified maximum-duration standard | 61.44 | % of cases complying with the specified maximum-duration standard | Yes | No | N/A | 4 | Scheduled Outage: Maximum Duration | 5654 | 3474 | 61.44%
2022-23 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Supply restored by 6:00 PM | 95 | % of cases in which supply was restored within the specified time | 71.43 | % of cases in which supply was restored within the specified time | Yes | No | N/A | 5 | Scheduled Outage: Restoration by 6:00 PM | 1442 | 1030 | 71.43%
2022-23 | Street Light Faults | Street Light Faults: Rectification of Line Faults | Rectification of line faults and restoration of streetlights. | Within 24 hours of detection or receipt of complaint, whichever is earlier | 90 | % of cases resolved within the specified time limit | N/A | Value reported as NIL | Yes | Yes | N/A | 6 | Street Light Faults: Line Faults | 0 | 0 | N/A (NIL / Municipal)
2022-23 | Street Light Faults | Street Light Faults: Replacement of Fused/Defective Unit | Replacement of a fused light or rectification/replacement of a defective street-light unit where the licensee is responsible for maintenance. | Within 24 hours of detection or receipt of complaint, whichever is earlier | 90 | % of cases resolved within the specified time limit | N/A | Value reported as NIL | Yes | Yes | N/A | 7 | Street Light Faults: Replacement of Defective Unit | 0 | 0 | N/A (NIL / Municipal)
2022-23 | Billing Performance | % Billing Mistakes | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | 0.1 | Maximum permissible % of bills requiring modification following complaints | 87.02 | % of cases resolved within the specified time limit | No | N/A | Different standard metric | 8 | % Billing Mistakes | 6318 | 5498 | 87.02%
2022-23 | Metering Performance | % Faulty Meters | Percentage of defective meters relative to the total number of meters in service. | N/A | 3 | Maximum permissible % of defective meters among meters in service | 72.55 | % of cases resolved within the specified time limit | No | N/A | Different standard metric | 9 | % Faulty Meters | 444846 | 322751 | 72.55%
2022-23 | Power Supply Quality | Frequency Variation | Variation in the frequency of the electricity supply from its prescribed frequency, | To maintain supply frequency within 49.0 Hz to 50.5 Hz | N/A | N/A | N/A | Value reported as NIL | No | N/A | Different standard metric | 10 | Frequency Variation | 0 | 0 | N/A (NIL / Perfect)
2022-23 | Power Supply Quality | Voltage Unbalance | Difference or imbalance in voltage at the point of commencement of supply, | Must not exceed 3% at the point of commencement of supply | N/A | N/A | 98.22 | % of cases resolved within the specified time limit | No | N/A | Different standard metric | 11 | Voltage Unbalance | 25114 | 24668 | 98.22%
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Restoration of Supply | Normal Fuse-Off Calls | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | Cities & towns: 4 working hours; Rural: 8 working hours | 99 | % of calls rectified within the specified time limits | DATA REPORTED BUT NOT READABLE | N/A | No | N/A | Data Unreadable
2023-24 | Restoration of Supply | Line Breakdowns | Restoration of power supply following an overhead line/cable breakdown. | Cities & towns: 6 hours; Rural: 24 hours | 95 | % of cases resolved within the specified time limit | DATA REPORTED BUT NOT READABLE | N/A | No | N/A | Data Unreadable
2023-24 | Scheduled Outage | Scheduled Outage: Maximum Duration in a Single Stretch | Duration of a scheduled power interruption, excluding load-shedding, which must not exceed the prescribed maximum duration. | Maximum 12 hours in a day | 95 | % of cases complying with the specified maximum-duration standard | DATA REPORTED BUT NOT READABLE | N/A | No | N/A | Data Unreadable
2023-24 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Supply restored by 6:00 PM | 95 | % of cases in which supply was restored within the specified time | DATA REPORTED BUT NOT READABLE | N/A | No | N/A | Data Unreadable
2023-24 | Street Light Faults | Street Light Faults: Rectification of Line Faults | Rectification of line faults and restoration of streetlights. | Within 24 hours of detection or receipt of complaint, whichever is earlier | 90 | % of cases resolved within the specified time limit | DATA REPORTED BUT NOT READABLE | N/A | No | N/A | Data Unreadable
2023-24 | Street Light Faults | Street Light Faults: Replacement of Fused/Defective Unit | Replacement of a fused light or rectification/replacement of a defective street-light unit where the licensee is responsible for maintenance. | Within 24 hours of detection or receipt of complaint, whichever is earlier | 90 | % of cases resolved within the specified time limit | DATA REPORTED BUT NOT READABLE | N/A | No | N/A | Data Unreadable
2023-24 | Billing Performance | % Billing Mistakes | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | 0.1 | Maximum permissible % of bills requiring modification following complaints | DATA REPORTED BUT NOT READABLE | N/A | No | N/A | Data Unreadable
2023-24 | Metering Performance | % Faulty Meters | Percentage of defective meters relative to the total number of meters in service. | N/A | 3 | Maximum permissible % of defective meters among meters in service | DATA REPORTED BUT NOT READABLE | N/A | No | N/A | Data Unreadable
2023-24 | Power Supply Quality | Frequency Variation | Variation in the frequency of the electricity supply from its prescribed frequency, | To maintain supply frequency within 49.0 Hz to 50.5 Hz | N/A | N/A | DATA REPORTED BUT NOT READABLE | N/A | No | N/A | Data Unreadable
2023-24 | Power Supply Quality | Voltage Unbalance | Difference or imbalance in voltage at the point of commencement of supply, | Must not exceed 3% at the point of commencement of supply | N/A | N/A | DATA REPORTED BUT NOT READABLE | N/A | No | N/A | Data Unreadable
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Restoration of Supply | Normal Fuse-Off Calls | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | Cities & towns: 4 working hours; Rural: 8 working hours | 99 | % of calls rectified within the specified time limits | OVERALL STD OF PERFORMANCE DATA NOT REPORTED. | N/A | No | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED.
2024-25 | Restoration of Supply | Line Breakdowns | Restoration of power supply following an overhead line/cable breakdown. | Cities & towns: 6 hours; Rural: 24 hours | 95 | % of cases resolved within the specified time limit | OVERALL STD OF PERFORMANCE DATA NOT REPORTED. | N/A | No | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED.
2024-25 | Scheduled Outage | Scheduled Outage: Maximum Duration in a Single Stretch | Duration of a scheduled power interruption, excluding load-shedding, which must not exceed the prescribed maximum duration. | Maximum 12 hours in a day | 95 | % of cases complying with the specified maximum-duration standard | OVERALL STD OF PERFORMANCE DATA NOT REPORTED. | N/A | No | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED.
2024-25 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Supply restored by 6:00 PM | 95 | % of cases in which supply was restored within the specified time | OVERALL STD OF PERFORMANCE DATA NOT REPORTED. | N/A | No | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED.
2024-25 | Street Light Faults | Street Light Faults: Rectification of Line Faults | Rectification of line faults and restoration of streetlights. | Within 24 hours of detection or receipt of complaint, whichever is earlier | 90 | % of cases resolved within the specified time limit | OVERALL STD OF PERFORMANCE DATA NOT REPORTED. | N/A | No | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED.
2024-25 | Street Light Faults | Street Light Faults: Replacement of Fused/Defective Unit | Replacement of a fused light or rectification/replacement of a defective street-light unit where the licensee is responsible for maintenance. | Within 24 hours of detection or receipt of complaint, whichever is earlier | 90 | % of cases resolved within the specified time limit | OVERALL STD OF PERFORMANCE DATA NOT REPORTED. | N/A | No | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED.
2024-25 | Billing Performance | % Billing Mistakes | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | 0.1 | Maximum permissible % of bills requiring modification following complaints | OVERALL STD OF PERFORMANCE DATA NOT REPORTED. | N/A | No | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED.
2024-25 | Metering Performance | % Faulty Meters | Percentage of defective meters relative to the total number of meters in service. | N/A | 3 | Maximum permissible % of defective meters among meters in service | OVERALL STD OF PERFORMANCE DATA NOT REPORTED. | N/A | No | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED.
2024-25 | Power Supply Quality | Frequency Variation | Variation in the frequency of the electricity supply from its prescribed frequency, | To maintain supply frequency within 49.0 Hz to 50.5 Hz | N/A | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED. | N/A | No | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED.
2024-25 | Power Supply Quality | Voltage Unbalance | Difference or imbalance in voltage at the point of commencement of supply, | Must not exceed 3% at the point of commencement of supply | N/A | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED. | N/A | No | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Restoration of Supply | Normal Fuse-Off Calls | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | Cities & towns: 4 working hours; Rural: 8 working hours | 99 | % of calls rectified within the specified time limits | OVERALL STD OF PERFORMANCE DATA NOT REPORTED. | N/A | No | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED.
2025-26 | Restoration of Supply | Line Breakdowns | Restoration of power supply following an overhead line/cable breakdown. | Cities & towns: 6 hours; Rural: 24 hours | 95 | % of cases resolved within the specified time limit | OVERALL STD OF PERFORMANCE DATA NOT REPORTED. | N/A | No | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED.
2025-26 | Scheduled Outage | Scheduled Outage: Maximum Duration in a Single Stretch | Duration of a scheduled power interruption, excluding load-shedding, which must not exceed the prescribed maximum duration. | Maximum 12 hours in a day | 95 | % of cases complying with the specified maximum-duration standard | OVERALL STD OF PERFORMANCE DATA NOT REPORTED. | N/A | No | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED.
2025-26 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Supply restored by 6:00 PM | 95 | % of cases in which supply was restored within the specified time | OVERALL STD OF PERFORMANCE DATA NOT REPORTED. | N/A | No | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED.
2025-26 | Street Light Faults | Street Light Faults: Rectification of Line Faults | Rectification of line faults and restoration of streetlights. | Within 24 hours of detection or receipt of complaint, whichever is earlier | 90 | % of cases resolved within the specified time limit | OVERALL STD OF PERFORMANCE DATA NOT REPORTED. | N/A | No | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED.
2025-26 | Street Light Faults | Street Light Faults: Replacement of Fused/Defective Unit | Replacement of a fused light or rectification/replacement of a defective street-light unit where the licensee is responsible for maintenance. | Within 24 hours of detection or receipt of complaint, whichever is earlier | 90 | % of cases resolved within the specified time limit | OVERALL STD OF PERFORMANCE DATA NOT REPORTED. | N/A | No | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED.
2025-26 | Billing Performance | % Billing Mistakes | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | 0.1 | Maximum permissible % of bills requiring modification following complaints | OVERALL STD OF PERFORMANCE DATA NOT REPORTED. | N/A | No | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED.
2025-26 | Metering Performance | % Faulty Meters | Percentage of defective meters relative to the total number of meters in service. | N/A | 3 | Maximum permissible % of defective meters among meters in service | OVERALL STD OF PERFORMANCE DATA NOT REPORTED. | N/A | No | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED.
2025-26 | Power Supply Quality | Frequency Variation | Variation in the frequency of the electricity supply from its prescribed frequency, | To maintain supply frequency within 49.0 Hz to 50.5 Hz | N/A | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED. | N/A | No | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED.
2025-26 | Power Supply Quality | Voltage Unbalance | Difference or imbalance in voltage at the point of commencement of supply, | Must not exceed 3% at the point of commencement of supply | N/A | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED. | N/A | No | N/A | OVERALL STD OF PERFORMANCE DATA NOT REPORTED.

## TGNPDCL, TELANGANA
Northern Power Distribution Company of Telangana Limited
Telangana State Electricity Regulatory Commission (Licensees’ Standards of Performance) Regulation, 2016.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Restoration of Supply | Normal Fuse-Off Calls | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | Cities & towns: 4 working hours; Rural: 8 working hours | 99 | % of calls rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2021-22 | Restoration of Supply | Line Breakdowns | Restoration of power supply following an overhead line/cable breakdown. | Cities & towns: 6 hours; Rural: 24 hours | 95 | % of cases resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2021-22 | Scheduled Outage | Scheduled Outage: Maximum Duration in a Single Stretch | Duration of a scheduled power interruption, excluding load-shedding, which must not exceed the prescribed maximum duration. | Maximum 12 hours in a day | 95 | % of cases complying with the specified maximum-duration standard | 100 | % of cases complying with the specified maximum-duration standard | Yes | Yes | N/A
2021-22 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Supply restored by 6:00 PM | 95 | % of cases in which supply was restored within the specified time | 100 | % of cases in which supply was restored within the specified time | Yes | Yes | N/A
2021-22 | Street Light Faults | Street Light Faults: Rectification of Line Faults | Rectification of line faults and restoration of streetlights. | Within 24 hours of detection or receipt of complaint, whichever is earlier | 90 | % of cases resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2021-22 | Street Light Faults | Street Light Faults: Replacement of Fused/Defective Unit | Replacement of a fused light or rectification/replacement of a defective street-light unit where the licensee is responsible for maintenance. | Within 24 hours of detection or receipt of complaint, whichever is earlier | 90 | % of cases resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2021-22 | Billing Performance | % Billing Mistakes | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | 0.1 | Maximum permissible % of bills requiring modification following complaints | 100 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
2021-22 | Metering Performance | % Faulty Meters | Percentage of defective meters relative to the total number of meters in service. | N/A | 3 | Maximum permissible % of defective meters among meters in service | 100 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
2021-22 | Power Supply Quality | Frequency Variation | Variation in the frequency of the electricity supply from its prescribed frequency, | To maintain supply frequency within 49.0 Hz to 50.5 Hz | N/A | N/A | 100 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
2021-22 | Power Supply Quality | Voltage Unbalance | Difference or imbalance in voltage at the point of commencement of supply, | Must not exceed 3% at the point of commencement of supply | N/A | N/A | 100 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Restoration of Supply | Normal Fuse-Off Calls | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | Cities & towns: 4 working hours; Rural: 8 working hours | 99 | % of calls rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2022-23 | Restoration of Supply | Line Breakdowns | Restoration of power supply following an overhead line/cable breakdown. | Cities & towns: 6 hours; Rural: 24 hours | 95 | % of cases resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2022-23 | Scheduled Outage | Scheduled Outage: Maximum Duration in a Single Stretch | Duration of a scheduled power interruption, excluding load-shedding, which must not exceed the prescribed maximum duration. | Maximum 12 hours in a day | 95 | % of cases complying with the specified maximum-duration standard | 100 | % of cases complying with the specified maximum-duration standard | Yes | Yes | N/A
2022-23 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Supply restored by 6:00 PM | 95 | % of cases in which supply was restored within the specified time | 100 | % of cases in which supply was restored within the specified time | Yes | Yes | N/A
2022-23 | Street Light Faults | Street Light Faults: Rectification of Line Faults | Rectification of line faults and restoration of streetlights. | Within 24 hours of detection or receipt of complaint, whichever is earlier | 90 | % of cases resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2022-23 | Street Light Faults | Street Light Faults: Replacement of Fused/Defective Unit | Replacement of a fused light or rectification/replacement of a defective street-light unit where the licensee is responsible for maintenance. | Within 24 hours of detection or receipt of complaint, whichever is earlier | 90 | % of cases resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2022-23 | Billing Performance | % Billing Mistakes | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | 0.1 | Maximum permissible % of bills requiring modification following complaints | 100 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
2022-23 | Metering Performance | % Faulty Meters | Percentage of defective meters relative to the total number of meters in service. | N/A | 3 | Maximum permissible % of defective meters among meters in service | 100 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
2022-23 | Power Supply Quality | Frequency Variation | Variation in the frequency of the electricity supply from its prescribed frequency, | To maintain supply frequency within 49.0 Hz to 50.5 Hz | N/A | N/A | 100 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
2022-23 | Power Supply Quality | Voltage Unbalance | Difference or imbalance in voltage at the point of commencement of supply, | Must not exceed 3% at the point of commencement of supply | N/A | N/A | 100 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Restoration of Supply | Normal Fuse-Off Calls | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | Cities & towns: 4 working hours; Rural: 8 working hours | 99 | % of calls rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2023-24 | Restoration of Supply | Line Breakdowns | Restoration of power supply following an overhead line/cable breakdown. | Cities & towns: 6 hours; Rural: 24 hours | 95 | % of cases resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2023-24 | Scheduled Outage | Scheduled Outage: Maximum Duration in a Single Stretch | Duration of a scheduled power interruption, excluding load-shedding, which must not exceed the prescribed maximum duration. | Maximum 12 hours in a day | 95 | % of cases complying with the specified maximum-duration standard | 100 | % of cases complying with the specified maximum-duration standard | Yes | Yes | N/A
2023-24 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Supply restored by 6:00 PM | 95 | % of cases in which supply was restored within the specified time | 100 | % of cases in which supply was restored within the specified time | Yes | Yes | N/A
2023-24 | Street Light Faults | Street Light Faults: Rectification of Line Faults | Rectification of line faults and restoration of streetlights. | Within 24 hours of detection or receipt of complaint, whichever is earlier | 90 | % of cases resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2023-24 | Street Light Faults | Street Light Faults: Replacement of Fused/Defective Unit | Replacement of a fused light or rectification/replacement of a defective street-light unit where the licensee is responsible for maintenance. | Within 24 hours of detection or receipt of complaint, whichever is earlier | 90 | % of cases resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2023-24 | Billing Performance | % Billing Mistakes | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | 0.1 | Maximum permissible % of bills requiring modification following complaints | 100 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
2023-24 | Metering Performance | % Faulty Meters | Percentage of defective meters relative to the total number of meters in service. | N/A | 3 | Maximum permissible % of defective meters among meters in service | 100 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
2023-24 | Power Supply Quality | Frequency Variation | Variation in the frequency of the electricity supply from its prescribed frequency, | To maintain supply frequency within 49.0 Hz to 50.5 Hz | N/A | N/A | 100 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
2023-24 | Power Supply Quality | Voltage Unbalance | Difference or imbalance in voltage at the point of commencement of supply, | Must not exceed 3% at the point of commencement of supply | N/A | N/A | 100 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Restoration of Supply | Normal Fuse-Off Calls | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | Cities & towns: 4 working hours; Rural: 8 working hours | 99 | % of calls rectified within the specified time limits | 99.97 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2024-25 | Restoration of Supply | Line Breakdowns | Restoration of power supply following an overhead line/cable breakdown. | Cities & towns: 6 hours; Rural: 24 hours | 95 | % of cases resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2024-25 | Scheduled Outage | Scheduled Outage: Maximum Duration in a Single Stretch | Duration of a scheduled power interruption, excluding load-shedding, which must not exceed the prescribed maximum duration. | Maximum 12 hours in a day | 95 | % of cases complying with the specified maximum-duration standard | 100 | % of cases complying with the specified maximum-duration standard | Yes | Yes | N/A
2024-25 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Supply restored by 6:00 PM | 95 | % of cases in which supply was restored within the specified time | 100 | % of cases in which supply was restored within the specified time | Yes | Yes | N/A
2024-25 | Street Light Faults | Street Light Faults: Rectification of Line Faults | Rectification of line faults and restoration of streetlights. | Within 24 hours of detection or receipt of complaint, whichever is earlier | 90 | % of cases resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2024-25 | Street Light Faults | Street Light Faults: Replacement of Fused/Defective Unit | Replacement of a fused light or rectification/replacement of a defective street-light unit where the licensee is responsible for maintenance. | Within 24 hours of detection or receipt of complaint, whichever is earlier | 90 | % of cases resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2024-25 | Billing Performance | % Billing Mistakes | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | 0.1 | Maximum permissible % of bills requiring modification following complaints | 99.73 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
2024-25 | Metering Performance | % Faulty Meters | Percentage of defective meters relative to the total number of meters in service. | N/A | 3 | Maximum permissible % of defective meters among meters in service | 99.93 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
2024-25 | Power Supply Quality | Frequency Variation | Variation in the frequency of the electricity supply from its prescribed frequency, | To maintain supply frequency within 49.0 Hz to 50.5 Hz | N/A | N/A | 100 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
2024-25 | Power Supply Quality | Voltage Unbalance | Difference or imbalance in voltage at the point of commencement of supply, | Must not exceed 3% at the point of commencement of supply | N/A | N/A | 100 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Restoration of Supply | Normal Fuse-Off Calls | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | Cities & towns: 4 working hours; Rural: 8 working hours | 99 | % of calls rectified within the specified time limits | 99.99 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2025-26 | Restoration of Supply | Line Breakdowns | Restoration of power supply following an overhead line/cable breakdown. | Cities & towns: 6 hours; Rural: 24 hours | 95 | % of cases resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2025-26 | Restoration of Supply | Distribution Transformer (DT) Failure | Restoration of supply through replacement of the distribution transformer following its failure. | Cities & towns: 24 hours; Rural: 48 hours | 95 | % of DTRs replaced within the specified time limits | 99.97 | % of DTRs replaced within the specified time limits | Yes | Yes | N/A
2025-26 | Scheduled Outage | Scheduled Outage: Maximum Duration in a Single Stretch | Duration of a scheduled power interruption, excluding load-shedding, which must not exceed the prescribed maximum duration. | Maximum 12 hours in a day | 95 | % of cases complying with the specified maximum-duration standard | 93.02 | % of cases complying with the specified maximum-duration standard | Yes | No | N/A
2025-26 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Supply restored by 6:00 PM | 95 | % of cases in which supply was restored within the specified time | 75.83 | % of cases in which supply was restored within the specified time | Yes | No | N/A
2025-26 | Street Light Faults | Street Light Faults: Rectification of Line Faults | Rectification of line faults and restoration of streetlights. | Within 24 hours of detection or receipt of complaint, whichever is earlier | 90 | % of cases resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2025-26 | Street Light Faults | Street Light Faults: Replacement of Fused/Defective Unit | Replacement of a fused light or rectification/replacement of a defective street-light unit where the licensee is responsible for maintenance. | Within 24 hours of detection or receipt of complaint, whichever is earlier | 90 | % of cases resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2025-26 | Billing Performance | % Billing Mistakes | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | 0.1 | Maximum permissible % of bills requiring modification following complaints | 99.88 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
2025-26 | Metering Performance | % Faulty Meters | Percentage of defective meters relative to the total number of meters in service. | N/A | 3 | Maximum permissible % of defective meters among meters in service | 99.99 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
2025-26 | Power Supply Quality | Frequency Variation | Variation in the frequency of the electricity supply from its prescribed frequency, | To maintain supply frequency within 49.0 Hz to 50.5 Hz | N/A | N/A | 100 | % of cases resolved within the specified time limit | No | N/A | Different standard metric
2025-26 | Power Supply Quality | Voltage Unbalance | Difference or imbalance in voltage at the point of commencement of supply, | Must not exceed 3% at the point of commencement of supply | N/A | N/A | 100 | % of cases resolved within the specified time limit | No | N/A | Different standard metric

## TPCODL,ODISHA
Tata Power Central Odisha Distribution Limited
ORISSA ELECTRICITY REGULATORY COMMISSION (LICENSEES' STANDARDS OF PERFORMANCE) REGULATIONS, 2004 | Orissa Electricity Regulatory Commission (Licensee’s Standard of Performance) (1st Amendment) Regulations, 2010.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Restoration of Supply | Fuse-off calls: Urban | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 6 hours in urban areas. | 90 | % of calls to be rectified within the specified time limits | 95 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2021-22 | Restoration of Supply | Fuse-off calls: Rural | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas. | 90 | % of calls to be rectified within the specified time limits | 93 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2021-22 | Restoration of Supply | Line breakdown: Urban | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 12 working hours in urban areas. | 95 | % of cases to be resolved within the specified time limit | 99.94 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2021-22 | Restoration of Supply | Line breakdown: Rural | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 24 hours in rural areas. | 95 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2021-22 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Maximum 12 hours in a day; supply must be restored by 6:00 PM during summer and 5:00PM during winter. | 90 | % of cases to comply with the specified maximum-duration standard | 100 | % of cases complying with the specified maximum-duration standard | Yes | Yes | N/A
2021-22 | Power Supply Quality | Supply frequency | Frequency of electricity supplied to consumers. | Maintain supply frequency within +/-3% of nominal frequency (50Hz) | N/A | N/A | -- | No. of hourly measurement in which the supply frequency went beyond + 3% | No | N/A | Reported data incomplete.
2021-22 | Power Supply Quality | Voltage Unbalance | Variation of supplied voltage from the declared voltage level. | Should not exceed 3% at the point of commencement of supply. | N/A | N/A | -- | No. of cases in which voltage at the point of commencement of supply exceeded 3% of the voltage limits. | No | N/A | Reported data incomplete.
2021-22 | Street Light Faults | Street light fault | Rectification of line faults. | N/A | 90 | % of cases to be resolved within the specified time limit | -- | % of cases resolved within the specified time limit | No | N/A | Reported data incomplete.
2021-22 | Metering Performance | Faulty bills | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | =<0.1 | % of bills requiring modifications following complaints to the total number of bills issued. | 0.46 | No. of faulty bills prepared as a percentage of total no. of bills issued | Yes | No | N/A
2021-22 | Restoration of Supply | Faulty/defective meters | Percentage of defective meters relative to the total number of meters in service. | The licensee must inspect the meter within 7 working days; replace a defective meter within 30 days, a burnt meter not attributable to the consumer within 30 working days, and a consumer-caused burnt meter within 15 days of payment after notifying the consumer within 7 days. | =<5% | % of faulty/ defective meters to the total number of meters in service, | 1.42 | No. of faulty/defective meters as a percentage of total no. of existing meters | Yes | Yes | N/A
2021-22 | Accidents | Fatal Human Accidents | Electrical accidents involving humans that result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 49 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2021-22 | Accidents | Fatal Animal Accidents | Electrical accidents involving animals that result in death. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 32 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2021-22 | Accidents | Non-fatal Human Accidents | Electrical accidents involving humans that do not result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 55 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2021-22 | Accidents | Non-fatal Animal Accidents | Electrical accidents involving animals that do not result in death | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 0 | No. of accident cases | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Restoration of Supply | Fuse-off calls: Urban | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 6 hours in urban areas. | 90 | % of calls to be rectified within the specified time limits | 98 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2022-23 | Restoration of Supply | Fuse-off calls: Rural | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas. | 90 | % of calls to be rectified within the specified time limits | 94 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2022-23 | Restoration of Supply | Line breakdown: Urban | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 12 working hours in urban areas. | 95 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2022-23 | Restoration of Supply | Line breakdown: Rural | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 24 hours in rural areas. | 95 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2022-23 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Maximum 12 hours in a day; supply must be restored by 6:00 PM during summer and 5:00PM during winter. | 90 | % of cases to comply with the specified maximum-duration standard | 100 | % of cases complying with the specified maximum-duration standard | Yes | Yes | N/A
2022-23 | Power Supply Quality | Supply frequency | Frequency of electricity supplied to consumers. | Maintain supply frequency within +/-3% of nominal frequency (50Hz) | N/A | N/A | -- | No. of hourly measurement in which the supply frequency went beyond + 3% | No | N/A | Reported data incomplete.
2022-23 | Power Supply Quality | Voltage Unbalance | Variation of supplied voltage from the declared voltage level. | Should not exceed 3% at the point of commencement of supply. | N/A | N/A | EHT: --; HT: --; LT: -- | No. of cases in which voltage at the point of commencement of supply exceeded 3% of the voltage limits. | No | N/A | Reported data incomplete.
2022-23 | Street Light Faults | Street light fault | Rectification of line faults. | N/A | 90 | % of cases to be resolved within the specified time limit | -- | % of cases resolved within the specified time limit | No | N/A | Reported data incomplete.
2022-23 | Metering Performance | Faulty bills | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | =<0.1 | % of bills requiring modifications following complaints to the total number of bills issued. | 0.1 | No. of faulty bills prepared as a percentage of total no. of bills issued | Yes | Yes | N/A
2022-23 | Restoration of Supply | Faulty/defective meters | Percentage of defective meters relative to the total number of meters in service. | The licensee must inspect the meter within 7 working days; replace a defective meter within 30 days, a burnt meter not attributable to the consumer within 30 working days, and a consumer-caused burnt meter within 15 days of payment after notifying the consumer within 7 days. | =<5% | % of faulty/ defective meters to the total number of meters in service, | 1.36 | No. of faulty/defective meters as a percentage of total no. of existing meters | Yes | Yes | N/A
2022-23 | Accidents | Fatal Human Accidents | Electrical accidents involving humans that result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 37 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2022-23 | Accidents | Fatal Animal Accidents | Electrical accidents involving animals that result in death. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 42 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2022-23 | Accidents | Non-fatal Human Accidents | Electrical accidents involving humans that do not result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 42 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2022-23 | Accidents | Non-fatal Animal Accidents | Electrical accidents involving animals that do not result in death | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 0 | No. of accident cases | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Restoration of Supply | Fuse-off calls: Urban | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 6 hours in urban areas. | 90 | % of calls to be rectified within the specified time limits | 94.83 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2023-24 | Restoration of Supply | Fuse-off calls: Rural | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas. | 90 | % of calls to be rectified within the specified time limits | 91.22 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2023-24 | Restoration of Supply | Line breakdown: Urban | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 12 working hours in urban areas. | 95 | % of cases to be resolved within the specified time limit | 99.96 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2023-24 | Restoration of Supply | Line breakdown: Rural | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 24 hours in rural areas. | 95 | % of cases to be resolved within the specified time limit | 99.99 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2023-24 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Maximum 12 hours in a day; supply must be restored by 6:00 PM during summer and 5:00PM during winter. | 90 | % of cases to comply with the specified maximum-duration standard | 97 | % of cases complying with the specified maximum-duration standard | Yes | Yes | N/A
2023-24 | Power Supply Quality | Supply frequency | Frequency of electricity supplied to consumers. | Maintain supply frequency within +/-3% of nominal frequency (50Hz) | N/A | N/A | -- | No. of hourly measurement in which the supply frequency went beyond + 3% | No | N/A | Reported data incomplete.
2023-24 | Power Supply Quality | Voltage Unbalance | Variation of supplied voltage from the declared voltage level. | Should not exceed 3% at the point of commencement of supply. | N/A | N/A | EHT: --; HT: --; LT: -- | No. of cases in which voltage at the point of commencement of supply exceeded 3% of the voltage limits. | No | N/A | Reported data incomplete.
2023-24 | Street Light Faults | Street light fault | Rectification of line faults. | N/A | 90 | % of cases to be resolved within the specified time limit | -- | % of cases resolved within the specified time limit | No | N/A | Reported data incomplete.
2023-24 | Metering Performance | Faulty bills | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | =<0.1 | % of bills requiring modifications following complaints to the total number of bills issued. | 0.08 | No. of faulty bills prepared as a percentage of total no. of bills issued | Yes | Yes | N/A
2023-24 | Restoration of Supply | Faulty/defective meters | Percentage of defective meters relative to the total number of meters in service. | The licensee must inspect the meter within 7 working days; replace a defective meter within 30 days, a burnt meter not attributable to the consumer within 30 working days, and a consumer-caused burnt meter within 15 days of payment after notifying the consumer within 7 days. | =<5% | % of faulty/ defective meters to the total number of meters in service, | 0.78 | No. of faulty/defective meters as a percentage of total no. of existing meters | Yes | Yes | N/A
2023-24 | Accidents | Fatal Human Accidents | Electrical accidents involving humans that result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 36 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2023-24 | Accidents | Fatal Animal Accidents | Electrical accidents involving animals that result in death. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 19 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2023-24 | Accidents | Non-fatal Human Accidents | Electrical accidents involving humans that do not result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 46 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2023-24 | Accidents | Non-fatal Animal Accidents | Electrical accidents involving animals that do not result in death | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 0 | No. of accident cases | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Restoration of Supply | Fuse-off calls: Urban | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 6 hours in urban areas. | 90 | % of calls to be rectified within the specified time limits | 92.27 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2024-25 | Restoration of Supply | Fuse-off calls: Rural | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas. | 90 | % of calls to be rectified within the specified time limits | 91.55 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2024-25 | Restoration of Supply | Line breakdown: Urban | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 12 working hours in urban areas. | 95 | % of cases to be resolved within the specified time limit | 99.84 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2024-25 | Restoration of Supply | Line breakdown: Rural | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 24 hours in rural areas. | 95 | % of cases to be resolved within the specified time limit | 99.94 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2024-25 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Maximum 12 hours in a day; supply must be restored by 6:00 PM during summer and 5:00PM during winter. | 90 | % of cases to comply with the specified maximum-duration standard | 99.69 | % of cases complying with the specified maximum-duration standard | Yes | Yes | N/A
2024-25 | Power Supply Quality | Supply frequency | Frequency of electricity supplied to consumers. | Maintain supply frequency within +/-3% of nominal frequency (50Hz) | N/A | N/A | -- | No. of hourly measurement in which the supply frequency went beyond + 3% | No | N/A | Reported data incomplete.
2024-25 | Power Supply Quality | Voltage Unbalance | Variation of supplied voltage from the declared voltage level. | Should not exceed 3% at the point of commencement of supply. | N/A | N/A | EHT: --; HT: --; LT: -- | No. of cases in which voltage at the point of commencement of supply exceeded 3% of the voltage limits. | No | N/A | Reported data incomplete.
2024-25 | Street Light Faults | Street light fault | Rectification of line faults. | N/A | 90 | % of cases to be resolved within the specified time limit | -- | % of cases resolved within the specified time limit | No | N/A | Reported data incomplete.
2024-25 | Metering Performance | Faulty bills | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | =<0.1 | % of bills requiring modifications following complaints to the total number of bills issued. | 0.02 | No. of faulty bills prepared as a percentage of total no. of bills issued | Yes | Yes | N/A
2024-25 | Restoration of Supply | Faulty/defective meters | Percentage of defective meters relative to the total number of meters in service. | The licensee must inspect the meter within 7 working days; replace a defective meter within 30 days, a burnt meter not attributable to the consumer within 30 working days, and a consumer-caused burnt meter within 15 days of payment after notifying the consumer within 7 days. | =<5% | % of faulty/ defective meters to the total number of meters in service, | 1.13 | No. of faulty/defective meters as a percentage of total no. of existing meters | Yes | Yes | N/A
2024-25 | Accidents | Fatal Human Accidents | Electrical accidents involving humans that result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 34 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2024-25 | Accidents | Fatal Animal Accidents | Electrical accidents involving animals that result in death. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 32 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2024-25 | Accidents | Non-fatal Human Accidents | Electrical accidents involving humans that do not result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 38 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2024-25 | Accidents | Non-fatal Animal Accidents | Electrical accidents involving animals that do not result in death | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 0 | No. of accident cases | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Restoration of Supply | Fuse-off calls: Urban | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 6 hours in urban areas. | 90 | % of calls to be rectified within the specified time limits | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Fuse-off calls: Rural | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas. | 90 | % of calls to be rectified within the specified time limits | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Line breakdown: Urban | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 12 working hours in urban areas. | 95 | % of cases to be resolved within the specified time limit | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Line breakdown: Rural | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 24 hours in rural areas. | 95 | % of cases to be resolved within the specified time limit | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Maximum 12 hours in a day; supply must be restored by 6:00 PM during summer and 5:00PM during winter. | 90 | % of cases to comply with the specified maximum-duration standard | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Power Supply Quality | Supply frequency | Frequency of electricity supplied to consumers. | Maintain supply frequency within +/-3% of nominal frequency (50Hz) | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Power Supply Quality | Voltage Unbalance | Variation of supplied voltage from the declared voltage level. | Should not exceed 3% at the point of commencement of supply. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Street Light Faults | Street light fault | Rectification of line faults. | N/A | 90 | % of cases to be resolved within the specified time limit | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Metering Performance | Faulty bills | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | =<0.1 | % of bills requiring modifications following complaints to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Faulty/defective meters | Percentage of defective meters relative to the total number of meters in service. | The licensee must inspect the meter within 7 working days; replace a defective meter within 30 days, a burnt meter not attributable to the consumer within 30 working days, and a consumer-caused burnt meter within 15 days of payment after notifying the consumer within 7 days. | =<5% | % of faulty/ defective meters to the total number of meters in service, | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Accidents | Fatal Human Accidents | Electrical accidents involving humans that result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Accidents | Fatal Animal Accidents | Electrical accidents involving animals that result in death. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Accidents | Non-fatal Human Accidents | Electrical accidents involving humans that do not result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Accidents | Non-fatal Animal Accidents | Electrical accidents involving animals that do not result in death | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.

## TPNODL,ODISHA
Tata Power North Odisha Distribution Limited
ORISSA ELECTRICITY REGULATORY COMMISSION (LICENSEES' STANDARDS OF PERFORMANCE) REGULATIONS, 2004 | Orissa Electricity Regulatory Commission (Licensee’s Standard of Performance) (1st Amendment) Regulations, 2010.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Restoration of Supply | Fuse-off calls: Urban | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 6 hours in urban areas. | 90 | % of calls to be rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2021-22 | Restoration of Supply | Fuse-off calls: Rural | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas. | 90 | % of calls to be rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2021-22 | Restoration of Supply | Line breakdown: Urban | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 12 working hours in urban areas. | 95 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2021-22 | Restoration of Supply | Line breakdown: Rural | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 24 hours in rural areas. | 95 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2021-22 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Maximum 12 hours in a day; supply must be restored by 6:00 PM during summer and 5:00PM during winter. | 90 | % of cases to comply with the specified maximum-duration standard | -- | % of cases complying with the specified maximum-duration standard | No | N/A | Reported data incomplete.
2021-22 | Power Supply Quality | Supply frequency | Frequency of electricity supplied to consumers. | Maintain supply frequency within +/-3% of nominal frequency (50Hz) | N/A | N/A | -- | No. of hourly measurement in which the supply frequency went beyond + 3% | No | N/A | Reported data incomplete.
2021-22 | Power Supply Quality | Voltage Unbalance | Variation of supplied voltage from the declared voltage level. | Should not exceed 3% at the point of commencement of supply. | N/A | N/A | -- | No. of cases in which voltage at the point of commencement of supply exceeded 3% of the voltage limits. | No | N/A | Reported data incomplete.
2021-22 | Street Light Faults | Street light fault | Rectification of line faults. | N/A | 90 | % of cases to be resolved within the specified time limit | -- | % of cases resolved within the specified time limit | No | N/A | Reported data incomplete.
2021-22 | Metering Performance | Faulty bills | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | =<0.1 | % of bills requiring modifications following complaints to the total number of bills issued. | 0.4 | No. of faulty bills prepared as a percentage of total no. of bills issued | Yes | No | N/A
2021-22 | Restoration of Supply | Faulty/defective meters | Percentage of defective meters relative to the total number of meters in service. | The licensee must inspect the meter within 7 working days; replace a defective meter within 30 days, a burnt meter not attributable to the consumer within 30 working days, and a consumer-caused burnt meter within 15 days of payment after notifying the consumer within 7 days. | =<5% | % of faulty/ defective meters to the total number of meters in service, | 14 | No. of faulty/defective meters as a percentage of total no. of existing meters | Yes | No | N/A
2021-22 | Accidents | Fatal Human Accidents | Electrical accidents involving humans that result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 3 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2021-22 | Accidents | Fatal Animal Accidents | Electrical accidents involving animals that result in death. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 9 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2021-22 | Accidents | Non-fatal Human Accidents | Electrical accidents involving humans that do not result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 11 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2021-22 | Accidents | Non-fatal Animal Accidents | Electrical accidents involving animals that do not result in death | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 0 | No. of accident cases | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Restoration of Supply | Fuse-off calls: Urban | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 6 hours in urban areas. | 90 | % of calls to be rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2022-23 | Restoration of Supply | Fuse-off calls: Rural | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas. | 90 | % of calls to be rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2022-23 | Restoration of Supply | Line breakdown: Urban | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 12 working hours in urban areas. | 95 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2022-23 | Restoration of Supply | Line breakdown: Rural | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 24 hours in rural areas. | 95 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2022-23 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Maximum 12 hours in a day; supply must be restored by 6:00 PM during summer and 5:00PM during winter. | 90 | % of cases to comply with the specified maximum-duration standard | -- | % of cases complying with the specified maximum-duration standard | No | N/A | Reported data incomplete.
2022-23 | Power Supply Quality | Supply frequency | Frequency of electricity supplied to consumers. | Maintain supply frequency within +/-3% of nominal frequency (50Hz) | N/A | N/A | -- | No. of hourly measurement in which the supply frequency went beyond + 3% | No | N/A | Reported data incomplete.
2022-23 | Power Supply Quality | Voltage Unbalance | Variation of supplied voltage from the declared voltage level. | Should not exceed 3% at the point of commencement of supply. | N/A | N/A | EHT: --; HT: --; LT: -- | No. of cases in which voltage at the point of commencement of supply exceeded 3% of the voltage limits. | No | N/A | Reported data incomplete.
2022-23 | Street Light Faults | Street light fault | Rectification of line faults. | N/A | 90 | % of cases to be resolved within the specified time limit | -- | % of cases resolved within the specified time limit | No | N/A | Reported data incomplete.
2022-23 | Metering Performance | Faulty bills | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | =<0.1 | % of bills requiring modifications following complaints to the total number of bills issued. | 1.49 | No. of faulty bills prepared as a percentage of total no. of bills issued | Yes | No | N/A
2022-23 | Restoration of Supply | Faulty/defective meters | Percentage of defective meters relative to the total number of meters in service. | The licensee must inspect the meter within 7 working days; replace a defective meter within 30 days, a burnt meter not attributable to the consumer within 30 working days, and a consumer-caused burnt meter within 15 days of payment after notifying the consumer within 7 days. | =<5% | % of faulty/ defective meters to the total number of meters in service, | 13 | No. of faulty/defective meters as a percentage of total no. of existing meters | Yes | No | N/A
2022-23 | Accidents | Fatal Human Accidents | Electrical accidents involving humans that result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 45 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2022-23 | Accidents | Fatal Animal Accidents | Electrical accidents involving animals that result in death. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 14 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2022-23 | Accidents | Non-fatal Human Accidents | Electrical accidents involving humans that do not result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 41 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2022-23 | Accidents | Non-fatal Animal Accidents | Electrical accidents involving animals that do not result in death | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 0 | No. of accident cases | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Restoration of Supply | Fuse-off calls: Urban | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 6 hours in urban areas. | 90 | % of calls to be rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2023-24 | Restoration of Supply | Fuse-off calls: Rural | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas. | 90 | % of calls to be rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2023-24 | Restoration of Supply | Line breakdown: Urban | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 12 working hours in urban areas. | 95 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2023-24 | Restoration of Supply | Line breakdown: Rural | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 24 hours in rural areas. | 95 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2023-24 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Maximum 12 hours in a day; supply must be restored by 6:00 PM during summer and 5:00PM during winter. | 90 | % of cases to comply with the specified maximum-duration standard | -- | No | No | N/A | Reported data incomplete.
2023-24 | Power Supply Quality | Supply frequency | Frequency of electricity supplied to consumers. | Maintain supply frequency within +/-3% of nominal frequency (50Hz) | N/A | N/A | -- | No | No | N/A | Reported data incomplete.
2023-24 | Power Supply Quality | Voltage Unbalance | Variation of supplied voltage from the declared voltage level. | Should not exceed 3% at the point of commencement of supply. | N/A | N/A | EHT: --; HT: --; LT: -- | No. of cases in which voltage at the point of commencement of supply exceeded 3% of the voltage limits. | No | N/A | Reported data incomplete.
2023-24 | Street Light Faults | Street light fault | Rectification of line faults. | N/A | 90 | % of cases to be resolved within the specified time limit | -- | % of cases resolved within the specified time limit | No | N/A | Reported data incomplete.
2023-24 | Metering Performance | Faulty bills | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | =<0.1 | % of bills requiring modifications following complaints to the total number of bills issued. | 1.44 | No. of faulty bills prepared as a percentage of total no. of bills issued | Yes | No | N/A
2023-24 | Restoration of Supply | Faulty/defective meters | Percentage of defective meters relative to the total number of meters in service. | The licensee must inspect the meter within 7 working days; replace a defective meter within 30 days, a burnt meter not attributable to the consumer within 30 working days, and a consumer-caused burnt meter within 15 days of payment after notifying the consumer within 7 days. | =<5% | % of faulty/ defective meters to the total number of meters in service, | 2.42 | No. of faulty/defective meters as a percentage of total no. of existing meters | Yes | Yes | N/A
2023-24 | Accidents | Fatal Human Accidents | Electrical accidents involving humans that result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 26 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2023-24 | Accidents | Fatal Animal Accidents | Electrical accidents involving animals that result in death. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 30 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2023-24 | Accidents | Non-fatal Human Accidents | Electrical accidents involving humans that do not result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 49 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2023-24 | Accidents | Non-fatal Animal Accidents | Electrical accidents involving animals that do not result in death | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 0 | No. of accident cases | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Restoration of Supply | Fuse-off calls: Urban | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 6 hours in urban areas. | 90 | % of calls to be rectified within the specified time limits | 100% | % of calls rectified within the specified time limits | Yes | Yes | N/A
2024-25 | Restoration of Supply | Fuse-off calls: Rural | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas. | 90 | % of calls to be rectified within the specified time limits | 100% | % of calls rectified within the specified time limits | Yes | Yes | N/A
2024-25 | Restoration of Supply | Line breakdown: Urban | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 12 working hours in urban areas. | 95 | % of cases to be resolved within the specified time limit | 100% | % of cases resolved within the specified time limit | Yes | Yes | N/A
2024-25 | Restoration of Supply | Line breakdown: Rural | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 24 hours in rural areas. | 95 | % of cases to be resolved within the specified time limit | 100% | % of cases resolved within the specified time limit | Yes | Yes | N/A
2024-25 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Maximum 12 hours in a day; supply must be restored by 6:00 PM during summer and 5:00PM during winter. | 90 | % of cases to comply with the specified maximum-duration standard | -- | % of cases complying with the specified maximum-duration standard | No | N/A | Reported data incomplete.
2024-25 | Power Supply Quality | Supply frequency | Frequency of electricity supplied to consumers. | Maintain supply frequency within +/-3% of nominal frequency (50Hz) | N/A | N/A | -- | No. of hourly measurement in which the supply frequency went beyond + 3% | No | N/A | Reported data incomplete.
2024-25 | Power Supply Quality | Voltage Unbalance | Variation of supplied voltage from the declared voltage level. | Should not exceed 3% at the point of commencement of supply. | N/A | N/A | EHT: --; HT: --; LT: -- | No. of cases in which voltage at the point of commencement of supply exceeded 3% of the voltage limits. | No | N/A | Reported data incomplete.
2024-25 | Street Light Faults | Street light fault | Rectification of line faults. | N/A | 90 | % of cases to be resolved within the specified time limit | -- | % of cases resolved within the specified time limit | No | N/A | Reported data incomplete.
2024-25 | Metering Performance | Faulty bills | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | =<0.1 | % of bills requiring modifications following complaints to the total number of bills issued. | 1.66% | No. of faulty bills prepared as a percentage of total no. of bills issued | Yes | No | N/A
2024-25 | Restoration of Supply | Faulty/defective meters | Percentage of defective meters relative to the total number of meters in service. | The licensee must inspect the meter within 7 working days; replace a defective meter within 30 days, a burnt meter not attributable to the consumer within 30 working days, and a consumer-caused burnt meter within 15 days of payment after notifying the consumer within 7 days. | =<5% | % of faulty/ defective meters to the total number of meters in service, | 1.2% | No. of faulty/defective meters as a percentage of total no. of existing meters | Yes | Yes | N/A
2024-25 | Accidents | Fatal Human Accidents | Electrical accidents involving humans that result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 24 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2024-25 | Accidents | Fatal Animal Accidents | Electrical accidents involving animals that result in death. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 20 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2024-25 | Accidents | Non-fatal Human Accidents | Electrical accidents involving humans that do not result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 19 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2024-25 | Accidents | Non-fatal Animal Accidents | Electrical accidents involving animals that do not result in death | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 0 | No. of accident cases | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Restoration of Supply | Fuse-off calls: Urban | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 6 hours in urban areas. | 90 | % of calls to be rectified within the specified time limits | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Fuse-off calls: Rural | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas. | 90 | % of calls to be rectified within the specified time limits | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Line breakdown: Urban | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 12 working hours in urban areas. | 95 | % of cases to be resolved within the specified time limit | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Line breakdown: Rural | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 24 hours in rural areas. | 95 | % of cases to be resolved within the specified time limit | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Maximum 12 hours in a day; supply must be restored by 6:00 PM during summer and 5:00PM during winter. | 90 | % of cases to comply with the specified maximum-duration standard | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Power Supply Quality | Supply frequency | Frequency of electricity supplied to consumers. | Maintain supply frequency within +/-3% of nominal frequency (50Hz) | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Power Supply Quality | Voltage Unbalance | Variation of supplied voltage from the declared voltage level. | Should not exceed 3% at the point of commencement of supply. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Street Light Faults | Street light fault | Rectification of line faults. | N/A | 90 | % of cases to be resolved within the specified time limit | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Metering Performance | Faulty bills | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | =<0.1 | % of bills requiring modifications following complaints to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Faulty/defective meters | Percentage of defective meters relative to the total number of meters in service. | The licensee must inspect the meter within 7 working days; replace a defective meter within 30 days, a burnt meter not attributable to the consumer within 30 working days, and a consumer-caused burnt meter within 15 days of payment after notifying the consumer within 7 days. | =<5% | % of faulty/ defective meters to the total number of meters in service, | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Accidents | Fatal Human Accidents | Electrical accidents involving humans that result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Accidents | Fatal Animal Accidents | Electrical accidents involving animals that result in death. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Accidents | Non-fatal Human Accidents | Electrical accidents involving humans that do not result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Accidents | Non-fatal Animal Accidents | Electrical accidents involving animals that do not result in death | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.

## TPSODL,ODISHA
Tata Power South Odisha Distribution Limited
ORISSA ELECTRICITY REGULATORY COMMISSION (LICENSEES' STANDARDS OF PERFORMANCE) REGULATIONS, 2004 | Orissa Electricity Regulatory Commission (Licensee’s Standard of Performance) (1st Amendment) Regulations, 2010.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Restoration of Supply | Fuse-off calls: Urban | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 6 hours in urban areas. | 90 | % of calls to be rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2021-22 | Restoration of Supply | Fuse-off calls: Rural | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas. | 90 | % of calls to be rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2021-22 | Restoration of Supply | Line breakdown: Urban | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 12 working hours in urban areas. | 95 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2021-22 | Restoration of Supply | Line breakdown: Rural | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 24 hours in rural areas. | 95 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2021-22 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Maximum 12 hours in a day; supply must be restored by 6:00 PM during summer and 5:00PM during winter. | 90 | % of cases to comply with the specified maximum-duration standard | -- | % of cases complying with the specified maximum-duration standard | No | N/A | Reported data incomplete.
2021-22 | Power Supply Quality | Supply frequency | Frequency of electricity supplied to consumers. | Maintain supply frequency within +/-3% of nominal frequency (50Hz) | N/A | N/A | -- | No. of hourly measurement in which the supply frequency went beyond + 3% | No | N/A | Reported data incomplete.
2021-22 | Power Supply Quality | Voltage Unbalance | Variation of supplied voltage from the declared voltage level. | Should not exceed 3% at the point of commencement of supply. | N/A | N/A | -- | No. of cases in which voltage at the point of commencement of supply exceeded 3% of the voltage limits. | No | N/A | Reported data incomplete.
2021-22 | Street Light Faults | Street light fault | Rectification of line faults. | N/A | 90 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2021-22 | Metering Performance | Faulty bills | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | =<0.1 | % of bills requiring modifications following complaints to the total number of bills issued. | 0.1 | No. of faulty bills prepared as a percentage of total no. of bills issued | Yes | Yes | N/A
2021-22 | Restoration of Supply | Faulty/defective meters | Percentage of defective meters relative to the total number of meters in service. | The licensee must inspect the meter within 7 working days; replace a defective meter within 30 days, a burnt meter not attributable to the consumer within 30 working days, and a consumer-caused burnt meter within 15 days of payment after notifying the consumer within 7 days. | =<5% | % of faulty/ defective meters to the total number of meters in service, | 8 | No. of faulty/defective meters as a percentage of total no. of existing meters | Yes | No | N/A
2021-22 | Accidents | Fatal Human Accidents | Electrical accidents involving humans that result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 37 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2021-22 | Accidents | Fatal Animal Accidents | Electrical accidents involving animals that result in death. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 9 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2021-22 | Accidents | Non-fatal Human Accidents | Electrical accidents involving humans that do not result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 30 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2021-22 | Accidents | Non-fatal Animal Accidents | Electrical accidents involving animals that do not result in death | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 0 | No. of accident cases | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Restoration of Supply | Fuse-off calls: Urban | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 6 hours in urban areas. | 90 | % of calls to be rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2022-23 | Restoration of Supply | Fuse-off calls: Rural | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas. | 90 | % of calls to be rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2022-23 | Restoration of Supply | Line breakdown: Urban | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 12 working hours in urban areas. | 95 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2022-23 | Restoration of Supply | Line breakdown: Rural | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 24 hours in rural areas. | 95 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2022-23 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Maximum 12 hours in a day; supply must be restored by 6:00 PM during summer and 5:00PM during winter. | 90 | % of cases to comply with the specified maximum-duration standard | -- | % of cases complying with the specified maximum-duration standard | No | N/A | Reported data incomplete.
2022-23 | Power Supply Quality | Supply frequency | Frequency of electricity supplied to consumers. | Maintain supply frequency within +/-3% of nominal frequency (50Hz) | N/A | N/A | -- | No. of hourly measurement in which the supply frequency went beyond + 3% | No | N/A | Reported data incomplete.
2022-23 | Power Supply Quality | Voltage Unbalance | Variation of supplied voltage from the declared voltage level. | Should not exceed 3% at the point of commencement of supply. | N/A | N/A | EHT: 0; HT: 0; LT: 0 | No. of cases in which voltage at the point of commencement of supply exceeded 3% of the voltage limits. | No | N/A | No benchmark defined in regulations.
2022-23 | Street Light Faults | Street light fault | Rectification of line faults. | N/A | 90 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2022-23 | Metering Performance | Faulty bills | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | =<0.1 | % of bills requiring modifications following complaints to the total number of bills issued. | 0.14 | No. of faulty bills prepared as a percentage of total no. of bills issued | Yes | No | N/A
2022-23 | Restoration of Supply | Faulty/defective meters | Percentage of defective meters relative to the total number of meters in service. | The licensee must inspect the meter within 7 working days; replace a defective meter within 30 days, a burnt meter not attributable to the consumer within 30 working days, and a consumer-caused burnt meter within 15 days of payment after notifying the consumer within 7 days. | =<5% | % of faulty/ defective meters to the total number of meters in service, | 2.29 | No. of faulty/defective meters as a percentage of total no. of existing meters | Yes | Yes | N/A
2022-23 | Accidents | Fatal Human Accidents | Electrical accidents involving humans that result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 29 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2022-23 | Accidents | Fatal Animal Accidents | Electrical accidents involving animals that result in death. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 17 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2022-23 | Accidents | Non-fatal Human Accidents | Electrical accidents involving humans that do not result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 41 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2022-23 | Accidents | Non-fatal Animal Accidents | Electrical accidents involving animals that do not result in death | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 0 | No. of accident cases | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Restoration of Supply | Fuse-off calls: Urban | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 6 hours in urban areas. | 90 | % of calls to be rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2023-24 | Restoration of Supply | Fuse-off calls: Rural | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas. | 90 | % of calls to be rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2023-24 | Restoration of Supply | Line breakdown: Urban | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 12 working hours in urban areas. | 95 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2023-24 | Restoration of Supply | Line breakdown: Rural | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 24 hours in rural areas. | 95 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2023-24 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Maximum 12 hours in a day; supply must be restored by 6:00 PM during summer and 5:00PM during winter. | 90 | % of cases to comply with the specified maximum-duration standard | -- | % of cases complying with the specified maximum-duration standard | No | N/A | Reported data incomplete.
2023-24 | Power Supply Quality | Supply frequency | Frequency of electricity supplied to consumers. | Maintain supply frequency within +/-3% of nominal frequency (50Hz) | N/A | N/A | -- | No. of hourly measurement in which the supply frequency went beyond + 3% | No | N/A | Reported data incomplete.
2023-24 | Power Supply Quality | Voltage Unbalance | Variation of supplied voltage from the declared voltage level. | Should not exceed 3% at the point of commencement of supply. | N/A | N/A | EHT: 0; HT: 0; LT: 0 | No. of cases in which voltage at the point of commencement of supply exceeded 3% of the voltage limits. | No | N/A | No benchmark defined in regulations.
2023-24 | Street Light Faults | Street light fault | Rectification of line faults. | N/A | 90 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2023-24 | Metering Performance | Faulty bills | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | =<0.1 | % of bills requiring modifications following complaints to the total number of bills issued. | 0.01 | No. of faulty bills prepared as a percentage of total no. of bills issued | Yes | Yes | N/A
2023-24 | Restoration of Supply | Faulty/defective meters | Percentage of defective meters relative to the total number of meters in service. | The licensee must inspect the meter within 7 working days; replace a defective meter within 30 days, a burnt meter not attributable to the consumer within 30 working days, and a consumer-caused burnt meter within 15 days of payment after notifying the consumer within 7 days. | =<5% | % of faulty/ defective meters to the total number of meters in service, | 4.48 | No. of faulty/defective meters as a percentage of total no. of existing meters | Yes | Yes | N/A
2023-24 | Accidents | Fatal Human Accidents | Electrical accidents involving humans that result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 20 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2023-24 | Accidents | Fatal Animal Accidents | Electrical accidents involving animals that result in death. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 6 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2023-24 | Accidents | Non-fatal Human Accidents | Electrical accidents involving humans that do not result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 18 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2023-24 | Accidents | Non-fatal Animal Accidents | Electrical accidents involving animals that do not result in death | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 0 | No. of accident cases | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Restoration of Supply | Fuse-off calls: Urban | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 6 hours in urban areas. | 90 | % of calls to be rectified within the specified time limits | 93.99% | % of calls rectified within the specified time limits | Yes | Yes | N/A
2024-25 | Restoration of Supply | Fuse-off calls: Rural | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas. | 90 | % of calls to be rectified within the specified time limits | 95.92% | % of calls rectified within the specified time limits | Yes | Yes | N/A
2024-25 | Restoration of Supply | Line breakdown: Urban | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 12 working hours in urban areas. | 95 | % of cases to be resolved within the specified time limit | 96.51% | % of cases resolved within the specified time limit | Yes | Yes | N/A
2024-25 | Restoration of Supply | Line breakdown: Rural | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 24 hours in rural areas. | 95 | % of cases to be resolved within the specified time limit | 97.07% | % of cases resolved within the specified time limit | Yes | Yes | N/A
2024-25 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Maximum 12 hours in a day; supply must be restored by 6:00 PM during summer and 5:00PM during winter. | 90 | % of cases to comply with the specified maximum-duration standard | -- | % of cases complying with the specified maximum-duration standard | No | N/A | Reported data incomplete.
2024-25 | Power Supply Quality | Supply frequency | Frequency of electricity supplied to consumers. | Maintain supply frequency within +/-3% of nominal frequency (50Hz) | N/A | N/A | -- | No. of hourly measurement in which the supply frequency went beyond + 3% | No | N/A | Reported data incomplete.
2024-25 | Power Supply Quality | Voltage Unbalance | Variation of supplied voltage from the declared voltage level. | Should not exceed 3% at the point of commencement of supply. | N/A | N/A | EHT: --; HT: --; LT: -- | No. of cases in which voltage at the point of commencement of supply exceeded 3% of the voltage limits. | No | N/A | No benchmark defined in regulations.
2024-25 | Street Light Faults | Street light fault | Rectification of line faults. | N/A | 90 | % of cases to be resolved within the specified time limit | 100% | % of cases resolved within the specified time limit | Yes | Yes | N/A
2024-25 | Metering Performance | Faulty bills | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | =<0.1 | % of bills requiring modifications following complaints to the total number of bills issued. | 0% | No. of faulty bills prepared as a percentage of total no. of bills issued | Yes | Yes | N/A
2024-25 | Restoration of Supply | Faulty/defective meters | Percentage of defective meters relative to the total number of meters in service. | The licensee must inspect the meter within 7 working days; replace a defective meter within 30 days, a burnt meter not attributable to the consumer within 30 working days, and a consumer-caused burnt meter within 15 days of payment after notifying the consumer within 7 days. | =<5% | % of faulty/ defective meters to the total number of meters in service, | 0.23% | No. of faulty/defective meters as a percentage of total no. of existing meters | Yes | Yes | N/A
2024-25 | Accidents | Fatal Human Accidents | Electrical accidents involving humans that result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 8 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2024-25 | Accidents | Fatal Animal Accidents | Electrical accidents involving animals that result in death. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 3 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2024-25 | Accidents | Non-fatal Human Accidents | Electrical accidents involving humans that do not result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 8 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2024-25 | Accidents | Non-fatal Animal Accidents | Electrical accidents involving animals that do not result in death | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 0 | No. of accident cases | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Restoration of Supply | Fuse-off calls: Urban | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 6 hours in urban areas. | 90 | % of calls to be rectified within the specified time limits | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Fuse-off calls: Rural | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas. | 90 | % of calls to be rectified within the specified time limits | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Line breakdown: Urban | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 12 working hours in urban areas. | 95 | % of cases to be resolved within the specified time limit | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Line breakdown: Rural | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 24 hours in rural areas. | 95 | % of cases to be resolved within the specified time limit | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Maximum 12 hours in a day; supply must be restored by 6:00 PM during summer and 5:00PM during winter. | 90 | % of cases to comply with the specified maximum-duration standard | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Power Supply Quality | Supply frequency | Frequency of electricity supplied to consumers. | Maintain supply frequency within +/-3% of nominal frequency (50Hz) | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Power Supply Quality | Voltage Unbalance | Variation of supplied voltage from the declared voltage level. | Should not exceed 3% at the point of commencement of supply. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Street Light Faults | Street light fault | Rectification of line faults. | N/A | 90 | % of cases to be resolved within the specified time limit | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Metering Performance | Faulty bills | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | =<0.1 | % of bills requiring modifications following complaints to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Faulty/defective meters | Percentage of defective meters relative to the total number of meters in service. | The licensee must inspect the meter within 7 working days; replace a defective meter within 30 days, a burnt meter not attributable to the consumer within 30 working days, and a consumer-caused burnt meter within 15 days of payment after notifying the consumer within 7 days. | =<5% | % of faulty/ defective meters to the total number of meters in service, | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Accidents | Fatal Human Accidents | Electrical accidents involving humans that result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Accidents | Fatal Animal Accidents | Electrical accidents involving animals that result in death. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Accidents | Non-fatal Human Accidents | Electrical accidents involving humans that do not result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Accidents | Non-fatal Animal Accidents | Electrical accidents involving animals that do not result in death | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.

## TPWODL,ODISHA
Tata Power West Odisha Distribution Limited
ORISSA ELECTRICITY REGULATORY COMMISSION (LICENSEES' STANDARDS OF PERFORMANCE) REGULATIONS, 2004 | Orissa Electricity Regulatory Commission (Licensee’s Standard of Performance) (1st Amendment) Regulations, 2010.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Restoration of Supply | Fuse-off calls: Urban | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 6 hours in urban areas. | 90 | % of calls to be rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2021-22 | Restoration of Supply | Fuse-off calls: Rural | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas. | 90 | % of calls to be rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2021-22 | Restoration of Supply | Line breakdown: Urban | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 12 working hours in urban areas. | 95 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2021-22 | Restoration of Supply | Line breakdown: Rural | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 24 hours in rural areas. | 95 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2021-22 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Maximum 12 hours in a day; supply must be restored by 6:00 PM during summer and 5:00PM during winter. | 90 | % of cases to comply with the specified maximum-duration standard | -- | % of cases complying with the specified maximum-duration standard | No | N/A | Reported data incomplete.
2021-22 | Power Supply Quality | Supply frequency | Frequency of electricity supplied to consumers. | Maintain supply frequency within +/-3% of nominal frequency (50Hz) | N/A | N/A | -- | No. of hourly measurement in which the supply frequency went beyond + 3% | No | N/A | Reported data incomplete.
2021-22 | Power Supply Quality | Voltage Unbalance | Variation of supplied voltage from the declared voltage level. | Should not exceed 3% at the point of commencement of supply. | N/A | N/A | -- | No. of cases in which voltage at the point of commencement of supply exceeded 3% of the voltage limits. | No | N/A | Reported data incomplete.
2021-22 | Street Light Faults | Street light fault | Rectification of line faults. | N/A | 90 | % of cases to be resolved within the specified time limit | 90 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2021-22 | Metering Performance | Faulty bills | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | =<0.1 | % of bills requiring modifications following complaints to the total number of bills issued. | 0.1 | No. of faulty bills prepared as a percentage of total no. of bills issued | Yes | Yes | N/A
2021-22 | Restoration of Supply | Faulty/defective meters | Percentage of defective meters relative to the total number of meters in service. | The licensee must inspect the meter within 7 working days; replace a defective meter within 30 days, a burnt meter not attributable to the consumer within 30 working days, and a consumer-caused burnt meter within 15 days of payment after notifying the consumer within 7 days. | =<5 | % of faulty/ defective meters to the total number of meters in service, | 5 | No. of faulty/defective meters as a percentage of total no. of existing meters | Yes | Yes | N/A
2021-22 | Accidents | Fatal Human Accidents | Electrical accidents involving humans that result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 2 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2021-22 | Accidents | Fatal Animal Accidents | Electrical accidents involving animals that result in death. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 53 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2021-22 | Accidents | Non-fatal Human Accidents | Electrical accidents involving humans that do not result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 16 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2021-22 | Accidents | Non-fatal Animal Accidents | Electrical accidents involving animals that do not result in death | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 0 | No. of accident cases | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Restoration of Supply | Fuse-off calls: Urban | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 6 hours in urban areas. | 90 | % of calls to be rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2022-23 | Restoration of Supply | Fuse-off calls: Rural | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas. | 90 | % of calls to be rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2022-23 | Restoration of Supply | Line breakdown: Urban | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 12 working hours in urban areas. | 95 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2022-23 | Restoration of Supply | Line breakdown: Rural | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 24 hours in rural areas. | 95 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2022-23 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Maximum 12 hours in a day; supply must be restored by 6:00 PM during summer and 5:00PM during winter. | 90 | % of cases to comply with the specified maximum-duration standard | 100 | % of cases complying with the specified maximum-duration standard | Yes | Yes | N/A
2022-23 | Power Supply Quality | Supply frequency | Frequency of electricity supplied to consumers. | Maintain supply frequency within +/-3% of nominal frequency (50Hz) | N/A | N/A | -- | No. of hourly measurement in which the supply frequency went beyond + 3% | No | N/A | No benchmark defined in regulations.
2022-23 | Power Supply Quality | Voltage Unbalance | Variation of supplied voltage from the declared voltage level. | Should not exceed 3% at the point of commencement of supply. | N/A | N/A | EHT: --; HT: 1.5; LT: -- | No. of cases in which voltage at the point of commencement of supply exceeded 3% of the voltage limits. | No | N/A | No benchmark defined in regulations.
2022-23 | Street Light Faults | Street light fault | Rectification of line faults. | N/A | 90 | % of cases to be resolved within the specified time limit | -- | % of cases resolved within the specified time limit | No | N/A | Reported data incomplete.
2022-23 | Metering Performance | Faulty bills | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | =<0.1 | % of bills requiring modifications following complaints to the total number of bills issued. | 0.0004 | No. of faulty bills prepared as a percentage of total no. of bills issued | Yes | Yes | N/A
2022-23 | Restoration of Supply | Faulty/defective meters | Percentage of defective meters relative to the total number of meters in service. | The licensee must inspect the meter within 7 working days; replace a defective meter within 30 days, a burnt meter not attributable to the consumer within 30 working days, and a consumer-caused burnt meter within 15 days of payment after notifying the consumer within 7 days. | =<5 | % of faulty/ defective meters to the total number of meters in service, | 0.0013 | No. of faulty/defective meters as a percentage of total no. of existing meters | Yes | Yes | N/A
2022-23 | Accidents | Fatal Human Accidents | Electrical accidents involving humans that result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 2 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2022-23 | Accidents | Fatal Animal Accidents | Electrical accidents involving animals that result in death. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 24 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2022-23 | Accidents | Non-fatal Human Accidents | Electrical accidents involving humans that do not result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 24 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2022-23 | Accidents | Non-fatal Animal Accidents | Electrical accidents involving animals that do not result in death | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 0 | No. of accident cases | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Restoration of Supply | Fuse-off calls: Urban | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 6 hours in urban areas. | 90 | % of calls to be rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2023-24 | Restoration of Supply | Fuse-off calls: Rural | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas. | 90 | % of calls to be rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2023-24 | Restoration of Supply | Line breakdown: Urban | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 12 working hours in urban areas. | 95 | % of cases to be resolved within the specified time limit | 99.96 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2023-24 | Restoration of Supply | Line breakdown: Rural | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 24 hours in rural areas. | 95 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2023-24 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Maximum 12 hours in a day; supply must be restored by 6:00 PM during summer and 5:00PM during winter. | 90 | % of cases to comply with the specified maximum-duration standard | 100 | % of cases complying with the specified maximum-duration standard | Yes | Yes | N/A
2023-24 | Power Supply Quality | Supply frequency | Frequency of electricity supplied to consumers. | Maintain supply frequency within +/-3% of nominal frequency (50Hz) | N/A | N/A | -- | No. of hourly measurement in which the supply frequency went beyond + 3% | No | N/A | Reported data incomplete.
2023-24 | Power Supply Quality | Voltage Unbalance | Variation of supplied voltage from the declared voltage level. | Should not exceed 3% at the point of commencement of supply. | N/A | N/A | EHT: --; HT: 9; LT: -- | No. of cases in which voltage at the point of commencement of supply exceeded 3% of the voltage limits. | No | N/A | No benchmark defined in regulations.
2023-24 | Street Light Faults | Street light fault | Rectification of line faults. | N/A | 90 | % of cases to be resolved within the specified time limit | -- | % of cases resolved within the specified time limit | No | N/A | Reported data incomplete.
2023-24 | Metering Performance | Faulty bills | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | =<0.1 | % of bills requiring modifications following complaints to the total number of bills issued. | 0.0005 | No. of faulty bills prepared as a percentage of total no. of bills issued | Yes | Yes | N/A
2023-24 | Restoration of Supply | Faulty/defective meters | Percentage of defective meters relative to the total number of meters in service. | The licensee must inspect the meter within 7 working days; replace a defective meter within 30 days, a burnt meter not attributable to the consumer within 30 working days, and a consumer-caused burnt meter within 15 days of payment after notifying the consumer within 7 days. | =<5 | % of faulty/ defective meters to the total number of meters in service, | 0.0836 | No. of faulty/defective meters as a percentage of total no. of existing meters | Yes | Yes | N/A
2023-24 | Accidents | Fatal Human Accidents | Electrical accidents involving humans that result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 46 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2023-24 | Accidents | Fatal Animal Accidents | Electrical accidents involving animals that result in death. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 46 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2023-24 | Accidents | Non-fatal Human Accidents | Electrical accidents involving humans that do not result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 44 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2023-24 | Accidents | Non-fatal Animal Accidents | Electrical accidents involving animals that do not result in death | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 0 | No. of accident cases | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Restoration of Supply | Fuse-off calls: Urban | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 6 hours in urban areas. | 90 | % of calls to be rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2024-25 | Restoration of Supply | Fuse-off calls: Rural | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas. | 90 | % of calls to be rectified within the specified time limits | 100 | % of calls rectified within the specified time limits | Yes | Yes | N/A
2024-25 | Restoration of Supply | Line breakdown: Urban | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 12 working hours in urban areas. | 95 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes |  | N/A
2024-25 | Restoration of Supply | Line breakdown: Rural | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 24 hours in rural areas. | 95 | % of cases to be resolved within the specified time limit | 100 | % of cases resolved within the specified time limit | Yes | Yes | N/A
2024-25 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Maximum 12 hours in a day; supply must be restored by 6:00 PM during summer and 5:00PM during winter. | 90 | % of cases to comply with the specified maximum-duration standard | 100 | % of cases complying with the specified maximum-duration standard | Yes | Yes | N/A
2024-25 | Power Supply Quality | Supply frequency | Frequency of electricity supplied to consumers. | Maintain supply frequency within +/-3% of nominal frequency (50Hz) | N/A | N/A | -- | No. of hourly measurement in which the supply frequency went beyond + 3% | No | N/A | Reported data incomplete.
2024-25 | Power Supply Quality | Voltage Unbalance | Variation of supplied voltage from the declared voltage level. | Should not exceed 3% at the point of commencement of supply. | N/A | N/A | EHT: --; HT: 0.08; LT: 0 | No. of cases in which voltage at the point of commencement of supply exceeded 3% of the voltage limits. | No | N/A | No benchmark defined in regulations.
2024-25 | Street Light Faults | Street light fault | Rectification of line faults. | N/A | 90 | % of cases to be resolved within the specified time limit | -- | % of cases resolved within the specified time limit | No | N/A | Reported data incomplete.
2024-25 | Metering Performance | Faulty bills | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | =<0.1 | % of bills requiring modifications following complaints to the total number of bills issued. | 0 | No. of faulty bills prepared as a percentage of total no. of bills issued | Yes | Yes | N/A
2024-25 | Restoration of Supply | Faulty/defective meters | Percentage of defective meters relative to the total number of meters in service. | The licensee must inspect the meter within 7 working days; replace a defective meter within 30 days, a burnt meter not attributable to the consumer within 30 working days, and a consumer-caused burnt meter within 15 days of payment after notifying the consumer within 7 days. | =<5 | % of faulty/ defective meters to the total number of meters in service, | 0.05 | No. of faulty/defective meters as a percentage of total no. of existing meters | Yes | Yes | N/A
2024-25 | Accidents | Fatal Human Accidents | Electrical accidents involving humans that result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 8 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2024-25 | Accidents | Fatal Animal Accidents | Electrical accidents involving animals that result in death. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 28 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2024-25 | Accidents | Non-fatal Human Accidents | Electrical accidents involving humans that do not result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 12 | No. of accident cases | No | N/A | No benchmark defined in regulations.
2024-25 | Accidents | Non-fatal Animal Accidents | Electrical accidents involving animals that do not result in death | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | 0 | No. of accident cases | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Restoration of Supply | Fuse-off calls: Urban | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 6 hours in urban areas. | 90 | % of calls to be rectified within the specified time limits | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Fuse-off calls: Rural | Restoration of supply for normal fuse-off calls, involving replacement of HG or LT fuses at the distribution transformer or consumer premises. | The distribution licensee must restore power supply following normal fuse-off calls within 24 hours in rural areas. | 90 | % of calls to be rectified within the specified time limits | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Line breakdown: Urban | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 12 working hours in urban areas. | 95 | % of cases to be resolved within the specified time limit | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Line breakdown: Rural | Restoration of power supply following an overhead line/cable breakdown. | The distribution licensee must restore power supply following line breakdowns within 24 hours in rural areas. | 95 | % of cases to be resolved within the specified time limit | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Scheduled Outage | Scheduled Outage: Restoration of Supply by 6:00 PM | Restoration of supply following a scheduled outage. | Maximum 12 hours in a day; supply must be restored by 6:00 PM during summer and 5:00PM during winter. | 90 | % of cases to comply with the specified maximum-duration standard | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Power Supply Quality | Supply frequency | Frequency of electricity supplied to consumers. | Maintain supply frequency within +/-3% of nominal frequency (50Hz) | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Power Supply Quality | Voltage Unbalance | Variation of supplied voltage from the declared voltage level. | Should not exceed 3% at the point of commencement of supply. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Street Light Faults | Street light fault | Rectification of line faults. | N/A | 90 | % of cases to be resolved within the specified time limit | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Metering Performance | Faulty bills | Percentage of bills requiring modification following complaints relative to the total number of bills issued. | N/A | =<0.1 | % of bills requiring modifications following complaints to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Faulty/defective meters | Percentage of defective meters relative to the total number of meters in service. | The licensee must inspect the meter within 7 working days; replace a defective meter within 30 days, a burnt meter not attributable to the consumer within 30 working days, and a consumer-caused burnt meter within 15 days of payment after notifying the consumer within 7 days. | =<5% | % of faulty/ defective meters to the total number of meters in service, | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Accidents | Fatal Human Accidents | Electrical accidents involving humans that result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Accidents | Fatal Animal Accidents | Electrical accidents involving animals that result in death. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Accidents | Non-fatal Human Accidents | Electrical accidents involving humans that do not result in fatality. | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Accidents | Non-fatal Animal Accidents | Electrical accidents involving animals that do not result in death | The Licensee shall endeavour to minimize electrical accidents in the distribution system. Increase or decrease in no. of electrical accidents compared over a period of time will be an indicator of the Licensee’s performance | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.

## AVVNL,RAJASTHAN
Ajmer Vidyut Vitran Nigam Limited
RERC ( Standards of Performance for Distribution Licensees) Regulations, 2021 | State that the RERC (Standards of Performance for Distribution Licensees) Regulations, 2021 came into force on 15 Apr 2021. It applies from 15 Apr 2021 onward; FY 2021-22 therefore starts before the regulation came into force.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Restoration of Supply | No current complaints | Restoring supply in case of supply-related problems/faults like blowing of HT/LT fuse/MCB prior to meter or at distribution transformer or loose connections at meter/service line. | Restore the supply within Class 1 Cities: Within 2 hours; Urban Areas: Within 4 hours; Rural Areas: Within 8 hours from reporting. | 95 | % of complaints to redressed in time | 99.04 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Restoration of Supply | Overhead Line/ overhead Cable breakdowns | Restoring supply after overhead line or overhead cable breakdowns. | Restore the supply within Class 1 Cities: Within 4 hours; Urban Areas: Within 6 hours; Rural Areas: Within 10 hours from occurrence. | 90 | % of complaints to redressed in time | 95.28 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Restoration of Supply | Underground cable break down | Restoring supply in case of its underground cable breakdown. | Restore the supply within Class 1 Cities: Within 12 hours; Urban Areas: Within 12 hours; Rural Areas: Within 24 hours from occurrence. | 90 | % of complaints to redressed in time | 97.95 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Restoration of Supply | Scheduled outage Default in 24 hours notice | Giving consumers advance notification of scheduled outages or planned shutdowns. | Notification of planned shutdowns must be given at least 24 hours in advance (and on the same day in emergent cases). | 90 | % of complaints to redressed in time | 99.16 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Restoration of Supply | Scheduled outage Exceeding 7 hours duration | The allowable duration limit of power supply interruptions in a day due to planned outages. | Interruption shall not exceed 7 hours in a day, and supply should normally be restored by 6 pm. | 90 | % of complaints to redressed in time | 98.15 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Meter Complaint | Testing of Meter | Verifying the correctness of a meter at site when a consumer reports that the meter is not functioning properly. | the licensee must verify the correctness of the meter at site and, if required, replace it within 15 days from the consumer's report | 90 | % of complaints to redressed in time | 98.29 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Meter Complaint | Replacement of stopped/defective/burned Meter | Replacing a consumer's meter that is detected or reported as stopped, damaged, or burnt. | Replace the meter within 24 hours in urban areas and 72 hours in rural areas from its detection or date of intimation by the consumer. | 90 | % of complaints to redressed in time | 98.4 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Meter Complaint | No-current complaint due to meter | Replacing a stopped, damaged, or burnt meter specifically when it causes a complete loss of supply (no current). | Replace the meter within 24 hours of reporting by the consumer or detection by the licensee (unless tempered, where it is replaced within 24 hours of consumer depositing security). | 90 | % of complaints to redressed in time | 98.89 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Shifting of Meters/Service Lines | Demand note | Inspecting and informing the consumer of the estimated cost of shifting meters or service lines. | Inspect and inform the estimated cost to the consumer ithin 15 days of receipt of application. | 90 | % of complaints to redressed in time | 96.78 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Shifting of Meters/Service Lines | Shifting of Meter | Shifting a consumer's meter after payment of the demand note and obtaining necessary clearances. | Shift the Meter for LT Consumers: Within 7 working days; HT & EHT Consumers: Within 15 working days from payment and clearance receipt. | 90 | % of complaints to redressed in time | 97.06 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Shifting of Meters/Service Lines | Shifting of Service line | Shifting a consumer's service line after payment of the demand note and obtaining necessary clearances. | Shift the service line for LT Consumers: Within 15 working days• HT Consumers: Within 1 month from payment and clearance receipt. | 90 | % of complaints to redressed in time | 97.89 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Release of New Connections or additional power | Release of new connection/additional power | Releasing new electricity connections or additional power to different categories of consumers. | Must be released as per the norms specified in the RERC (Supply Code & Connected Matters) Regulations, 2021. | 90 | % of complaints to redressed in time | 98.53 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Transfer of ownership or change of category | Transfer of ownership or change of category | Transferring the ownership of connection or changing the category of supply on the existing system. | Ownership of the connection or change of category on the existing system shall be transferred within 1 month from receipt of necessary documents certifying the transfer/change. | 90 | % of complaints to redressed in time | 99.13 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Disconnection of supply | Disconnection of supply | Disconnecting supply upon consumer request and clearance of dues. | Disconnect the supply in Class 1 Cities: Within 3 working days; Urban & Rural Areas: Within 7 working days from receipt of request and clearance. | 90 | % of complaints to redressed in time | 99.25 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Disconnection of supply | Issue of no dues certificate | Refunding security/money and issuing a "No-Dues Certificate" upon permanent disconnection. | Shall issue the certificate within 7 days from the date of disconnection or from the date of clearing the admissible dues, whichever is later. | 90 | % of complaints to redressed in time | 99.57 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Restoration of a Disconnected Consumer | Restoration of DC consumers | Restoring power supply to a disconnected (DC) consumer after they clear their dues. | Restore the supply within 6 working hours of clearing the dues (if infrastructure erection is required, as per RERC Supply Code Regulations, 2021). | 90 | % of complaints to redressed in time | 98.91 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Delivery of Bills | Timely delivery of bills | Serving regular electricity bills on the consumers. | Served as per the timelines given in the RERC (Supply Code & Connected Matters) Regulations, 2021 (and within 7 days of written complaint if the first bill is delayed). | 90 | % of complaints to redressed in time | 98.75 | % of complaints redressal in time | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Restoration of Supply | No current complaints | Restoring supply in case of supply-related problems/faults like blowing of HT/LT fuse/MCB prior to meter or at distribution transformer or loose connections at meter/service line. | Restore the supply within Class 1 Cities: Within 2 hours; Urban Areas: Within 4 hours; Rural Areas: Within 8 hours from reporting. | 95 | % of complaints to redressed in time | 98.77 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Restoration of Supply | Overhead Line/ overhead Cable breakdowns | Restoring supply after overhead line or overhead cable breakdowns. | Restore the supply within Class 1 Cities: Within 4 hours; Urban Areas: Within 6 hours; Rural Areas: Within 10 hours from occurrence. | 90 | % of complaints to redressed in time | 94.39 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Restoration of Supply | Underground cable break down | Restoring supply in case of its underground cable breakdown. | Restore the supply within Class 1 Cities: Within 12 hours; Urban Areas: Within 12 hours; Rural Areas: Within 24 hours from occurrence. | 90 | % of complaints to redressed in time | 92.95 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Restoration of Supply | Scheduled outage Default in 24 hours notice | Giving consumers advance notification of scheduled outages or planned shutdowns. | Notification of planned shutdowns must be given at least 24 hours in advance (and on the same day in emergent cases). | 90 | % of complaints to redressed in time | 99.1 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Restoration of Supply | Scheduled outage Exceeding 7 hours duration | The allowable duration limit of power supply interruptions in a day due to planned outages. | Interruption shall not exceed 7 hours in a day, and supply should normally be restored by 6 pm. | 90 | % of complaints to redressed in time | 96.28 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Meter Complaint | Testing of Meter | Verifying the correctness of a meter at site when a consumer reports that the meter is not functioning properly. | the licensee must verify the correctness of the meter at site and, if required, replace it within 15 days from the consumer's report | 90 | % of complaints to redressed in time | 98.3 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Meter Complaint | Replacement of stopped/defective/burned Meter | Replacing a consumer's meter that is detected or reported as stopped, damaged, or burnt. | Replace the meter within 24 hours in urban areas and 72 hours in rural areas from its detection or date of intimation by the consumer. | 90 | % of complaints to redressed in time | 98.27 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Meter Complaint | No-current complaint due to meter | Replacing a stopped, damaged, or burnt meter specifically when it causes a complete loss of supply (no current). | Replace the meter within 24 hours of reporting by the consumer or detection by the licensee (unless tempered, where it is replaced within 24 hours of consumer depositing security). | 90 | % of complaints to redressed in time | 98.45 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Shifting of Meters/Service Lines | Demand note | Inspecting and informing the consumer of the estimated cost of shifting meters or service lines. | Inspect and inform the estimated cost to the consumer ithin 15 days of receipt of application. | 90 | % of complaints to redressed in time | 96.39 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Shifting of Meters/Service Lines | Shifting of Meter | Shifting a consumer's meter after payment of the demand note and obtaining necessary clearances. | Shift the Meter for LT Consumers: Within 7 working days; HT & EHT Consumers: Within 15 working days from payment and clearance receipt. | 90 | % of complaints to redressed in time | 96.45 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Shifting of Meters/Service Lines | Shifting of Service line | Shifting a consumer's service line after payment of the demand note and obtaining necessary clearances. | Shift the service line for LT Consumers: Within 15 working days; HT Consumers: Within 1 month from payment and clearance receipt. | 90 | % of complaints to redressed in time | 97.95 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Release of New Connections or additional power | Release of new connection/additional power | Releasing new electricity connections or additional power to different categories of consumers. | Must be released as per the norms specified in the RERC (Supply Code & Connected Matters) Regulations, 2021. | 90 | % of complaints to redressed in time | 97.4 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Transfer of ownership or change of category | Transfer of ownership or change of category | Transferring the ownership of connection or changing the category of supply on the existing system. | Ownership of the connection or change of category on the existing system shall be transferred within 1 month from receipt of necessary documents certifying the transfer/change. | 90 | % of complaints to redressed in time | 95.41 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Disconnection of supply | Disconnection of supply | Disconnecting supply upon consumer request and clearance of dues. | Disconnect the supply in Class 1 Cities: Within 3 working days; Urban & Rural Areas: Within 7 working days from receipt of request and clearance. | 90 | % of complaints to redressed in time | 97.57 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Disconnection of supply | Issue of no dues certificate | Refunding security/money and issuing a "No-Dues Certificate" upon permanent disconnection. | Shall issue the certificate within 7 days from the date of disconnection or from the date of clearing the admissible dues, whichever is later. | 90 | % of complaints to redressed in time | 100 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Restoration of a Disconnected Consumer | Restoration of DC consumers | Restoring power supply to a disconnected (DC) consumer after they clear their dues. | Restore the supply within 6 working hours of clearing the dues. | 90 | % of complaints to redressed in time | 98.57 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Delivery of Bills | Timely delivery of bills | Serving regular electricity bills on the consumers. | Served as per the timelines given in the RERC (Supply Code & Connected Matters) Regulations, 2021 (and within 7 days of written complaint if the first bill is delayed). | 90 | % of complaints to redressed in time | 99.47 | % of complaints redressal in time | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Restoration of Supply | No current complaints | Restoring supply in case of supply-related problems/faults like blowing of HT/LT fuse/MCB prior to meter or at distribution transformer or loose connections at meter/service line. | Restore the supply within Class 1 Cities: Within 2 hours; Urban Areas: Within 4 hours; Rural Areas: Within 8 hours from reporting. | 95 | % of complaints to redressed in time | 98.83 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Restoration of Supply | Overhead Line/ overhead Cable breakdowns | Restoring supply after overhead line or overhead cable breakdowns. | Restore the supply within Class 1 Cities: Within 4 hours; Urban Areas: Within 6 hours; Rural Areas: Within 10 hours from occurrence. | 90 | % of complaints to redressed in time | 93.77 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Restoration of Supply | Underground cable break down | Restoring supply in case of its underground cable breakdown. | Restore the supply within Class 1 Cities: Within 12 hours; Urban Areas: Within 12 hours; Rural Areas: Within 24 hours from occurrence. | 90 | % of complaints to redressed in time | 96.24 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Restoration of Supply | Scheduled outage Default in 24 hours notice | Giving consumers advance notification of scheduled outages or planned shutdowns. | Notification of planned shutdowns must be given at least 24 hours in advance (and on the same day in emergent cases). | 90 | % of complaints to redressed in time | 99.47 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Restoration of Supply | Scheduled outage Exceeding 7 hours duration | The allowable duration limit of power supply interruptions in a day due to planned outages. | Interruption shall not exceed 7 hours in a day, and supply should normally be restored by 6 pm. | 90 | % of complaints to redressed in time | 96.7 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Meter Complaint | Testing of Meter | Verifying the correctness of a meter at site when a consumer reports that the meter is not functioning properly. | the licensee must verify the correctness of the meter at site and, if required, replace it within 15 days from the consumer's report | 90 | % of complaints to redressed in time | 98.53 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Meter Complaint | Replacement of stopped/defective/burned Meter | Replacing a consumer's meter that is detected or reported as stopped, damaged, or burnt. | Replace the meter within 24 hours in urban areas and 72 hours in rural areas from its detection or date of intimation by the consumer. | 90 | % of complaints to redressed in time | 99.56 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Meter Complaint | No-current complaint due to meter | Replacing a stopped, damaged, or burnt meter specifically when it causes a complete loss of supply (no current). | Replace the meter within 24 hours of reporting by the consumer or detection by the licensee (unless tempered, where it is replaced within 24 hours of consumer depositing security). | 90 | % of complaints to redressed in time | 99.44 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Shifting of Meters/Service Lines | Demand note | Inspecting and informing the consumer of the estimated cost of shifting meters or service lines. | Inspect and inform the estimated cost to the consumer ithin 15 days of receipt of application. | 90 | % of complaints to redressed in time | 98.51 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Shifting of Meters/Service Lines | Shifting of Meter | Shifting a consumer's meter after payment of the demand note and obtaining necessary clearances. | Shift the Meter for LT Consumers: Within 7 working days; HT & EHT Consumers: Within 15 working days from payment and clearance receipt. | 90 | % of complaints to redressed in time | 96.35 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Shifting of Meters/Service Lines | Shifting of Service line | Shifting a consumer's service line after payment of the demand note and obtaining necessary clearances. | Shift the service line for LT Consumers: Within 15 working days• HT Consumers: Within 1 month from payment and clearance receipt. | 90 | % of complaints to redressed in time | 97.29 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Release of New Connections or additional power | Release of new connection/additional power | Releasing new electricity connections or additional power to different categories of consumers. | Must be released as per the norms specified in the RERC (Supply Code & Connected Matters) Regulations, 2021. | 90 | % of complaints to redressed in time | 97.73 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Transfer of ownership or change of category | Transfer of ownership or change of category | Transferring the ownership of connection or changing the category of supply on the existing system. | Ownership of the connection or change of category on the existing system shall be transferred within 1 month from receipt of necessary documents certifying the transfer/change. | 90 | % of complaints to redressed in time | 98.25 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Disconnection of supply | Disconnection of supply | Disconnecting supply upon consumer request and clearance of dues. | Disconnect the supply in Class 1 Cities: Within 3 working days; Urban & Rural Areas: Within 7 working days from receipt of request and clearance. | 90 | % of complaints to redressed in time | 96.8 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Disconnection of supply | Issue of no dues certificate | Refunding security/money and issuing a "No-Dues Certificate" upon permanent disconnection. | Shall issue the certificate within 7 days from the date of disconnection or from the date of clearing the admissible dues, whichever is later. | 90 | % of complaints to redressed in time | 100 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Restoration of a Disconnected Consumer | Restoration of DC consumers | Restoring power supply to a disconnected (DC) consumer after they clear their dues. | Restore the supply within 6 working hours of clearing the dues (if infrastructure erection is required, as per RERC Supply Code Regulations, 2021). | 90 | % of complaints to redressed in time | 98.06 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Delivery of Bills | Timely delivery of bills | Serving regular electricity bills on the consumers. | Served as per the timelines given in the RERC (Supply Code & Connected Matters) Regulations, 2021 (and within 7 days of written complaint if the first bill is delayed). | 90 | % of complaints to redressed in time | 98.73 | % of complaints redressal in time | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Restoration of Supply | No current complaints | Restoring supply in case of supply-related problems/faults like blowing of HT/LT fuse/MCB prior to meter or at distribution transformer or loose connections at meter/service line. | Restore the supply within Class 1 Cities: Within 2 hours; Urban Areas: Within 4 hours; Rural Areas: Within 8 hours from reporting. | 95 | % of complaints to redressed in time | 98.93 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Restoration of Supply | Overhead Line/ overhead Cable breakdowns | Restoring supply after overhead line or overhead cable breakdowns. | Restore the supply within Class 1 Cities: Within 4 hours; Urban Areas: Within 6 hours; Rural Areas: Within 10 hours from occurrence. | 90 | % of complaints to redressed in time | 94.49 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Restoration of Supply | Underground cable break down | Restoring supply in case of its underground cable breakdown. | Restore the supply within Class 1 Cities: Within 12 hours; Urban Areas: Within 12 hours; Rural Areas: Within 24 hours from occurrence. | 90 | % of complaints to redressed in time | 97.11 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Restoration of Supply | Scheduled outage Default in 24 hours notice | Giving consumers advance notification of scheduled outages or planned shutdowns. | Notification of planned shutdowns must be given at least 24 hours in advance (and on the same day in emergent cases). | 90 | % of complaints to redressed in time | 99.89 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Restoration of Supply | Scheduled outage Exceeding 7 hours duration | The allowable duration limit of power supply interruptions in a day due to planned outages. | Interruption shall not exceed 7 hours in a day, and supply should normally be restored by 6 pm. | 90 | % of complaints to redressed in time | 95.22 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Meter Complaint | Testing of Meter | Verifying the correctness of a meter at site when a consumer reports that the meter is not functioning properly. | the licensee must verify the correctness of the meter at site and, if required, replace it within 15 days from the consumer's report | 90 | % of complaints to redressed in time | 97.88 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Meter Complaint | Replacement of stopped/defective/burned Meter | Replacing a consumer's meter that is detected or reported as stopped, damaged, or burnt. | Replace the meter within 24 hours in urban areas and 72 hours in rural areas from its detection or date of intimation by the consumer. | 90 | % of complaints to redressed in time | 98.59 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Meter Complaint | No-current complaint due to meter | Replacing a stopped, damaged, or burnt meter specifically when it causes a complete loss of supply (no current). | Replace the meter within 24 hours of reporting by the consumer or detection by the licensee (unless tempered, where it is replaced within 24 hours of consumer depositing security). | 90 | % of complaints to redressed in time | 99.7 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Shifting of Meters/Service Lines | Demand note | Inspecting and informing the consumer of the estimated cost of shifting meters or service lines. | Inspect and inform the estimated cost to the consumer ithin 15 days of receipt of application. | 90 | % of complaints to redressed in time | 98.05 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Shifting of Meters/Service Lines | Shifting of Meter | Shifting a consumer's meter after payment of the demand note and obtaining necessary clearances. | Shift the Meter for LT Consumers: Within 7 working days; HT & EHT Consumers: Within 15 working days from payment and clearance receipt. | 90 | % of complaints to redressed in time | 97.91 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Shifting of Meters/Service Lines | Shifting of Service line | Shifting a consumer's service line after payment of the demand note and obtaining necessary clearances. | Shift the service line for LT Consumers: Within 15 working days• HT Consumers: Within 1 month from payment and clearance receipt. | 90 | % of complaints to redressed in time | 94.76 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Release of New Connections or additional power | Release of new connection/additional power | Releasing new electricity connections or additional power to different categories of consumers. | Must be released as per the norms specified in the RERC (Supply Code & Connected Matters) Regulations, 2021. | 90 | % of complaints to redressed in time | 95.34 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Transfer of ownership or change of category | Transfer of ownership or change of category | Transferring the ownership of connection or changing the category of supply on the existing system. | Ownership of the connection or change of category on the existing system shall be transferred within 1 month from receipt of necessary documents certifying the transfer/change. | 90 | % of complaints to redressed in time | 98.08 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Disconnection of supply | Disconnection of supply | Disconnecting supply upon consumer request and clearance of dues. | Disconnect the supply in Class 1 Cities: Within 3 working days; Urban & Rural Areas: Within 7 working days from receipt of request and clearance. | 90 | % of complaints to redressed in time | 95.59 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Disconnection of supply | Issue of no dues certificate | Refunding security/money and issuing a "No-Dues Certificate" upon permanent disconnection. | Shall issue the certificate within 7 days from the date of disconnection or from the date of clearing the admissible dues, whichever is later. | 90 | % of complaints to redressed in time | 95.39 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Restoration of a Disconnected Consumer | Restoration of DC consumers | Restoring power supply to a disconnected (DC) consumer after they clear their dues. | Restore the supply within 6 working hours of clearing the dues (if infrastructure erection is required, as per RERC Supply Code Regulations, 2021). | 90 | % of complaints to redressed in time | 98.77 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Delivery of Bills | Timely delivery of bills | Serving regular electricity bills on the consumers. | Served as per the timelines given in the RERC (Supply Code & Connected Matters) Regulations, 2021 (and within 7 days of written complaint if the first bill is delayed). | 90 | % of complaints to redressed in time | 95.52 | % of complaints redressal in time | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Restoration of Supply | No current complaints | Restoring supply in case of supply-related problems/faults like blowing of HT/LT fuse/MCB prior to meter or at distribution transformer or loose connections at meter/service line. | Restore the supply within Class 1 Cities: Within 2 hours; Urban Areas: Within 4 hours; Rural Areas: Within 8 hours from reporting. | 95 | % of complaints to redressed in time | 99.36 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Restoration of Supply | Overhead Line/ overhead Cable breakdowns | Restoring supply after overhead line or overhead cable breakdowns. | Restore the supply within Class 1 Cities: Within 4 hours; Urban Areas: Within 6 hours; Rural Areas: Within 10 hours from occurrence. | 90 | % of complaints to redressed in time | 95.35 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Restoration of Supply | Underground cable break down | Restoring supply in case of its underground cable breakdown. | Restore the supply within Class 1 Cities: Within 12 hours; Urban Areas: Within 12 hours; Rural Areas: Within 24 hours from occurrence. | 90 | % of complaints to redressed in time | 95.35 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Restoration of Supply | Scheduled outage Default in 24 hours notice | Giving consumers advance notification of scheduled outages or planned shutdowns. | Notification of planned shutdowns must be given at least 24 hours in advance (and on the same day in emergent cases). | 90 | % of complaints to redressed in time | 99.76 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Restoration of Supply | Scheduled outage Exceeding 7 hours duration | The allowable duration limit of power supply interruptions in a day due to planned outages. | Interruption shall not exceed 7 hours in a day, and supply should normally be restored by 6 pm. | 90 | % of complaints to redressed in time | 95.01 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Meter Complaint | Testing of Meter | Verifying the correctness of a meter at site when a consumer reports that the meter is not functioning properly. | the licensee must verify the correctness of the meter at site and, if required, replace it within 15 days from the consumer's report | 90 | % of complaints to redressed in time | 98.01 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Meter Complaint | Replacement of stopped/defective/burned Meter | Replacing a consumer's meter that is detected or reported as stopped, damaged, or burnt. | Replace the meter within 24 hours in urban areas and 72 hours in rural areas from its detection or date of intimation by the consumer. | 90 | % of complaints to redressed in time | 98.42 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Meter Complaint | No-current complaint due to meter | Replacing a stopped, damaged, or burnt meter specifically when it causes a complete loss of supply (no current). | Replace the meter within 24 hours of reporting by the consumer or detection by the licensee (unless tempered, where it is replaced within 24 hours of consumer depositing security). | 90 | % of complaints to redressed in time | 99.83 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Shifting of Meters/Service Lines | Demand note | Inspecting and informing the consumer of the estimated cost of shifting meters or service lines. | Inspect and inform the estimated cost to the consumer ithin 15 days of receipt of application. | 90 | % of complaints to redressed in time | 98.57 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Shifting of Meters/Service Lines | Shifting of Meter | Shifting a consumer's meter after payment of the demand note and obtaining necessary clearances. | Shift the Meter for LT Consumers: Within 7 working days; HT & EHT Consumers: Within 15 working days from payment and clearance receipt. | 90 | % of complaints to redressed in time | 95.8 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Shifting of Meters/Service Lines | Shifting of Service line | Shifting a consumer's service line after payment of the demand note and obtaining necessary clearances. | Shift the service line for LT Consumers: Within 15 working days• HT Consumers: Within 1 month from payment and clearance receipt. | 90 | % of complaints to redressed in time | 95.92 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Release of New Connections or additional power | Release of new connection/additional power | Releasing new electricity connections or additional power to different categories of consumers. | Must be released as per the norms specified in the RERC (Supply Code & Connected Matters) Regulations, 2021. | 90 | % of complaints to redressed in time | 96.64 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Transfer of ownership or change of category | Transfer of ownership or change of category | Transferring the ownership of connection or changing the category of supply on the existing system. | Ownership of the connection or change of category on the existing system shall be transferred within 1 month from receipt of necessary documents certifying the transfer/change. | 90 | % of complaints to redressed in time | 98.62 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Disconnection of supply | Disconnection of supply | Disconnecting supply upon consumer request and clearance of dues. | Disconnect the supply in Class 1 Cities: Within 3 working days; Urban & Rural Areas: Within 7 working days from receipt of request and clearance. | 90 | % of complaints to redressed in time | 97.01 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Disconnection of supply | Issue of no dues certificate | Refunding security/money and issuing a "No-Dues Certificate" upon permanent disconnection. | Shall issue the certificate within 7 days from the date of disconnection or from the date of clearing the admissible dues, whichever is later. | 90 | % of complaints to redressed in time | 96.6 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Restoration of a Disconnected Consumer | Restoration of DC consumers | Restoring power supply to a disconnected (DC) consumer after they clear their dues. | Restore the supply within 6 working hours of clearing the dues (if infrastructure erection is required, as per RERC Supply Code Regulations, 2021). | 90 | % of complaints to redressed in time | 98.85 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Delivery of Bills | Timely delivery of bills | Serving regular electricity bills on the consumers. | Served as per the timelines given in the RERC (Supply Code & Connected Matters) Regulations, 2021 (and within 7 days of written complaint if the first bill is delayed). | 90 | % of complaints to redressed in time | 98.37 | % of complaints redressal in time | Yes | Yes | N/A

## JVVNL,RAJASTHAN
Jaipur Vidyut Vitran Nigam Limited
RERC ( Standards of Performance for Distribution Licensees) Regulations, 2021 | State that the RERC (Standards of Performance for Distribution Licensees) Regulations, 2021 came into force on 15 Apr 2021. It applies from 15 Apr 2021 onward; FY 2021-22 therefore starts before the regulation came into force.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Restoration of Supply | No current complaints | Restoring supply in case of supply-related problems/faults like blowing of HT/LT fuse/MCB prior to meter or at distribution transformer or loose connections at meter/service line. | Restore the supply within Class 1 Cities: Within 2 hours; Urban Areas: Within 4 hours; Rural Areas: Within 8 hours from reporting. | 95 | % of complaints to redressed in time | 98.3 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Restoration of Supply | Overhead Line/ overhead Cable breakdowns | Restoring supply after overhead line or overhead cable breakdowns. | Restore the supply within Class 1 Cities: Within 4 hours; Urban Areas: Within 6 hours; Rural Areas: Within 10 hours from occurrence. | 90 | % of complaints to redressed in time | 98.92 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Restoration of Supply | Underground cable break down | Restoring supply in case of its underground cable breakdown. | Restore the supply within Class 1 Cities: Within 12 hours; Urban Areas: Within 12 hours; Rural Areas: Within 24 hours from occurrence. | 90 | % of complaints to redressed in time | 99.78 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Restoration of Supply | Scheduled outage Default in 24 hours notice | Giving consumers advance notification of scheduled outages or planned shutdowns. | Notification of planned shutdowns must be given at least 24 hours in advance (and on the same day in emergent cases). | 90 | % of complaints to redressed in time | 96.77 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Restoration of Supply | Scheduled outage Exceeding 7 hours duration | The allowable duration limit of power supply interruptions in a day due to planned outages. | Interruption shall not exceed 7 hours in a day, and supply should normally be restored by 6 pm. | 90 | % of complaints to redressed in time | 99.34% | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Meter Complaint | Testing of Meter | Verifying the correctness of a meter at site when a consumer reports that the meter is not functioning properly. | Replace the meter within 15 days from the date of reporting by the consumer. | 90 | % of complaints to redressed in time | 98.62 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Meter Complaint | Replacement of stopped/defective/burned Meter | Replacing a consumer's meter that is detected or reported as stopped, damaged, or burnt. | Replace the meter within 24 hours in urban areas and 72 hours in rural areas from its detection or date of intimation by the consumer. | 90 | % of complaints to redressed in time | 96.97 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Meter Complaint | No-current complaint due to meter | Replacing a stopped, damaged, or burnt meter specifically when it causes a complete loss of supply (no current). | Replace the meter within 24 hours of reporting by the consumer or detection by the licensee (unless tempered, where it is replaced within 24 hours of consumer depositing security). | 90 | % of complaints to redressed in time | 96.9 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Shifting of Meters/Service Lines | Demand note | Inspecting and informing the consumer of the estimated cost of shifting meters or service lines. | Inspect and inform the estimated cost to the consumer ithin 15 days of receipt of application. | 90 | % of complaints to redressed in time | 98.82 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Shifting of Meters/Service Lines | Shifting of Meter | Shifting a consumer's meter after payment of the demand note and obtaining necessary clearances. | Shift the Meter for LT Consumers: Within 7 working days; HT & EHT Consumers: Within 15 working days from payment and clearance receipt. | 90 | % of complaints to redressed in time | 97.42 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Shifting of Meters/Service Lines | Shifting of Service line | Shifting a consumer's service line after payment of the demand note and obtaining necessary clearances. | Shift the service line for LT Consumers: Within 15 working days• HT Consumers: Within 1 month from payment and clearance receipt. | 90 | % of complaints to redressed in time | 95.38 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Release of New Connections or additional power | Release of new connection/additional power | Releasing new electricity connections or additional power to different categories of consumers. | Must be released as per the norms specified in the RERC (Supply Code & Connected Matters) Regulations, 2021. | 90 | % of complaints to redressed in time | 98.31 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Transfer of ownership or change of category | Transfer of ownership or change of category | Transferring the ownership of connection or changing the category of supply on the existing system. | Ownership of the connection or change of category on the existing system shall be transferred within 1 month from receipt of necessary documents certifying the transfer/change. | 90 | % of complaints to redressed in time | 96.88 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Disconnection of supply | Disconnection of supply | Disconnecting supply upon consumer request and clearance of dues. | Disconnect the supply in Class 1 Cities: Within 3 working days; Urban & Rural Areas: Within 7 working days from receipt of request and clearance. | 90 | % of complaints to redressed in time | 99.42 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Disconnection of supply | Issue of no dues certificate | Refunding security/money and issuing a "No-Dues Certificate" upon permanent disconnection. | Shall issue the certificate within 7 days from the date of disconnection or from the date of clearing the admissible dues, whichever is later. | 90 | % of complaints to redressed in time | 98.99 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Restoration of a Disconnected Consumer | Restoration of DC consumers | Restoring power supply to a disconnected (DC) consumer after they clear their dues. | Restore the supply within 6 working hours of clearing the dues (if infrastructure erection is required, as per RERC Supply Code Regulations, 2021). | 90 | % of complaints to redressed in time | 99.21 | % of complaints redressal in time | Yes | Yes | N/A
2021-22 | Delivery of Bills | Timely delivery of bills | Serving regular electricity bills on the consumers. | Served as per the timelines given in the RERC (Supply Code & Connected Matters) Regulations, 2021 (and within 7 days of written complaint if the first bill is delayed). | 90 | % of complaints to redressed in time | 99.94 | % of complaints redressal in time | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Restoration of Supply | No current complaints | Restoring supply in case of supply-related problems/faults like blowing of HT/LT fuse/MCB prior to meter or at distribution transformer or loose connections at meter/service line. | Restore the supply within Class 1 Cities: Within 2 hours; Urban Areas: Within 4 hours; Rural Areas: Within 8 hours from reporting. | 95 | % of complaints to redressed in time | 98.4 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Restoration of Supply | Overhead Line/ overhead Cable breakdowns | Restoring supply after overhead line or overhead cable breakdowns. | Restore the supply within Class 1 Cities: Within 4 hours; Urban Areas: Within 6 hours; Rural Areas: Within 10 hours from occurrence. | 90 | % of complaints to redressed in time | 98.65 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Restoration of Supply | Underground cable break down | Restoring supply in case of its underground cable breakdown. | Restore the supply within Class 1 Cities: Within 12 hours; Urban Areas: Within 12 hours; Rural Areas: Within 24 hours from occurrence. | 90 | % of complaints to redressed in time | 99.01 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Restoration of Supply | Scheduled outage Default in 24 hours notice | Giving consumers advance notification of scheduled outages or planned shutdowns. | Notification of planned shutdowns must be given at least 24 hours in advance (and on the same day in emergent cases). | 90 | % of complaints to redressed in time | 97.08 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Restoration of Supply | Scheduled outage Exceeding 7 hours duration | The allowable duration limit of power supply interruptions in a day due to planned outages. | Interruption shall not exceed 7 hours in a day, and supply should normally be restored by 6 pm. | 90 | % of complaints to redressed in time | 99.52 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Meter Complaint | Testing of Meter | Verifying the correctness of a meter at site when a consumer reports that the meter is not functioning properly. | Replace the meter within 15 days from the date of reporting by the consumer. | 90 | % of complaints to redressed in time | 96.56 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Meter Complaint | Replacement of stopped/defective/burned Meter | Replacing a consumer's meter that is detected or reported as stopped, damaged, or burnt. | Replace the meter within 24 hours in urban areas and 72 hours in rural areas from its detection or date of intimation by the consumer. | 90 | % of complaints to redressed in time | 96.72 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Meter Complaint | No-current complaint due to meter | Replacing a stopped, damaged, or burnt meter specifically when it causes a complete loss of supply (no current). | Replace the meter within 24 hours of reporting by the consumer or detection by the licensee (unless tempered, where it is replaced within 24 hours of consumer depositing security). | 90 | % of complaints to redressed in time | 97.98 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Shifting of Meters/Service Lines | Demand note | Inspecting and informing the consumer of the estimated cost of shifting meters or service lines. | Inspect and inform the estimated cost to the consumer ithin 15 days of receipt of application. | 90 | % of complaints to redressed in time | 98.3 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Shifting of Meters/Service Lines | Shifting of Meter | Shifting a consumer's meter after payment of the demand note and obtaining necessary clearances. | Shift the Meter for LT Consumers: Within 7 working days; HT & EHT Consumers: Within 15 working days from payment and clearance receipt. | 90 | % of complaints to redressed in time | 97.26 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Shifting of Meters/Service Lines | Shifting of Service line | Shifting a consumer's service line after payment of the demand note and obtaining necessary clearances. | Shift the service line for LT Consumers: Within 15 working days; HT Consumers: Within 1 month from payment and clearance receipt. | 90 | % of complaints to redressed in time | 96.79 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Release of New Connections or additional power | Release of new connection/additional power | Releasing new electricity connections or additional power to different categories of consumers. | Must be released as per the norms specified in the RERC (Supply Code & Connected Matters) Regulations, 2021. | 90 | % of complaints to redressed in time | 98.99 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Transfer of ownership or change of category | Transfer of ownership or change of category | Transferring the ownership of connection or changing the category of supply on the existing system. | Ownership of the connection or change of category on the existing system shall be transferred within 1 month from receipt of necessary documents certifying the transfer/change. | 90 | % of complaints to redressed in time | 98.84 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Disconnection of supply | Disconnection of supply | Disconnecting supply upon consumer request and clearance of dues. | Disconnect the supply in Class 1 Cities: Within 3 working days; Urban & Rural Areas: Within 7 working days from receipt of request and clearance. | 90 | % of complaints to redressed in time | 99.85 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Disconnection of supply | Issue of no dues certificate | Refunding security/money and issuing a "No-Dues Certificate" upon permanent disconnection. | Shall issue the certificate within 7 days from the date of disconnection or from the date of clearing the admissible dues, whichever is later. | 90 | % of complaints to redressed in time | 99.39 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Restoration of a Disconnected Consumer | Restoration of DC consumers | Restoring power supply to a disconnected (DC) consumer after they clear their dues. | Restore the supply within 6 working hours of clearing the dues. | 90 | % of complaints to redressed in time | 99.42 | % of complaints redressal in time | Yes | Yes | N/A
2022-23 | Delivery of Bills | Timely delivery of bills | Serving regular electricity bills on the consumers. | Served as per the timelines given in the RERC (Supply Code & Connected Matters) Regulations, 2021 (and within 7 days of written complaint if the first bill is delayed). | 90 | % of complaints to redressed in time | 99.69 | % of complaints redressal in time | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Restoration of Supply | No current complaints | Restoring supply in case of supply-related problems/faults like blowing of HT/LT fuse/MCB prior to meter or at distribution transformer or loose connections at meter/service line. | Restore the supply within Class 1 Cities: Within 2 hours; Urban Areas: Within 4 hours; Rural Areas: Within 8 hours from reporting. | 95 | % of complaints to redressed in time | 98.35 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Restoration of Supply | Overhead Line/ overhead Cable breakdowns | Restoring supply after overhead line or overhead cable breakdowns. | Restore the supply within Class 1 Cities: Within 4 hours; Urban Areas: Within 6 hours; Rural Areas: Within 10 hours from occurrence. | 90 | % of complaints to redressed in time | 98.92 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Restoration of Supply | Underground cable break down | Restoring supply in case of its underground cable breakdown. | Restore the supply within Class 1 Cities: Within 12 hours; Urban Areas: Within 12 hours; Rural Areas: Within 24 hours from occurrence. | 90 | % of complaints to redressed in time | 99.86 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Restoration of Supply | Scheduled outage Default in 24 hours notice | Giving consumers advance notification of scheduled outages or planned shutdowns. | Notification of planned shutdowns must be given at least 24 hours in advance (and on the same day in emergent cases). | 90 | % of complaints to redressed in time | 97.71 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Restoration of Supply | Scheduled outage Exceeding 7 hours duration | The allowable duration limit of power supply interruptions in a day due to planned outages. | Interruption shall not exceed 7 hours in a day, and supply should normally be restored by 6 pm. | 90 | % of complaints to redressed in time | 98.29 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Meter Complaint | Testing of Meter | Verifying the correctness of a meter at site when a consumer reports that the meter is not functioning properly. | Replace the meter within 15 days from the date of reporting by the consumer. | 90 | % of complaints to redressed in time | 98.11 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Meter Complaint | Replacement of stopped/defective/burned Meter | Replacing a consumer's meter that is detected or reported as stopped, damaged, or burnt. | Replace the meter within 24 hours in urban areas and 72 hours in rural areas from its detection or date of intimation by the consumer. | 90 | % of complaints to redressed in time | 97.13 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Meter Complaint | No-current complaint due to meter | Replacing a stopped, damaged, or burnt meter specifically when it causes a complete loss of supply (no current). | Replace the meter within 24 hours of reporting by the consumer or detection by the licensee (unless tempered, where it is replaced within 24 hours of consumer depositing security). | 90 | % of complaints to redressed in time | 97.26 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Shifting of Meters/Service Lines | Demand note | Inspecting and informing the consumer of the estimated cost of shifting meters or service lines. | Inspect and inform the estimated cost to the consumer ithin 15 days of receipt of application. | 90 | % of complaints to redressed in time | 98.79 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Shifting of Meters/Service Lines | Shifting of Meter | Shifting a consumer's meter after payment of the demand note and obtaining necessary clearances. | Shift the Meter for LT Consumers: Within 7 working days; HT & EHT Consumers: Within 15 working days from payment and clearance receipt. | 90 | % of complaints to redressed in time | 95.86 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Shifting of Meters/Service Lines | Shifting of Service line | Shifting a consumer's service line after payment of the demand note and obtaining necessary clearances. | Shift the service line for LT Consumers: Within 15 working days• HT Consumers: Within 1 month from payment and clearance receipt. | 90 | % of complaints to redressed in time | 95.87 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Release of New Connections or additional power | Release of new connection/additional power | Releasing new electricity connections or additional power to different categories of consumers. | Must be released as per the norms specified in the RERC (Supply Code & Connected Matters) Regulations, 2021. | 90 | % of complaints to redressed in time | 98.57 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Transfer of ownership or change of category | Transfer of ownership or change of category | Transferring the ownership of connection or changing the category of supply on the existing system. | Ownership of the connection or change of category on the existing system shall be transferred within 1 month from receipt of necessary documents certifying the transfer/change. | 90 | % of complaints to redressed in time | 98.52 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Disconnection of supply | Disconnection of supply | Disconnecting supply upon consumer request and clearance of dues. | Disconnect the supply in Class 1 Cities: Within 3 working days; Urban & Rural Areas: Within 7 working days from receipt of request and clearance. | 90 | % of complaints to redressed in time | 97.41 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Disconnection of supply | Issue of no dues certificate | Refunding security/money and issuing a "No-Dues Certificate" upon permanent disconnection. | Shall issue the certificate within 7 days from the date of disconnection or from the date of clearing the admissible dues, whichever is later. | 90 | % of complaints to redressed in time | 99.5 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Restoration of a Disconnected Consumer | Restoration of DC consumers | Restoring power supply to a disconnected (DC) consumer after they clear their dues. | Restore the supply within 6 working hours of clearing the dues (if infrastructure erection is required, as per RERC Supply Code Regulations, 2021). | 90 | % of complaints to redressed in time | 99.75 | % of complaints redressal in time | Yes | Yes | N/A
2023-24 | Delivery of Bills | Timely delivery of bills | Serving regular electricity bills on the consumers. | Served as per the timelines given in the RERC (Supply Code & Connected Matters) Regulations, 2021 (and within 7 days of written complaint if the first bill is delayed). | 90 | % of complaints to redressed in time | 98.51 | % of complaints redressal in time | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Restoration of Supply | No current complaints | Restoring supply in case of supply-related problems/faults like blowing of HT/LT fuse/MCB prior to meter or at distribution transformer or loose connections at meter/service line. | Restore the supply within Class 1 Cities: Within 2 hours; Urban Areas: Within 4 hours; Rural Areas: Within 8 hours from reporting. | 95 | % of complaints to redressed in time | 99.28 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Restoration of Supply | Overhead Line/ overhead Cable breakdowns | Restoring supply after overhead line or overhead cable breakdowns. | Restore the supply within Class 1 Cities: Within 4 hours; Urban Areas: Within 6 hours; Rural Areas: Within 10 hours from occurrence. | 90 | % of complaints to redressed in time | 99.15 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Restoration of Supply | Underground cable break down | Restoring supply in case of its underground cable breakdown. | Restore the supply within Class 1 Cities: Within 12 hours; Urban Areas: Within 12 hours; Rural Areas: Within 24 hours from occurrence. | 90 | % of complaints to redressed in time | 99.49 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Restoration of Supply | Scheduled outage Default in 24 hours notice | Giving consumers advance notification of scheduled outages or planned shutdowns. | Notification of planned shutdowns must be given at least 24 hours in advance (and on the same day in emergent cases). | 90 | % of complaints to redressed in time | 99.32 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Restoration of Supply | Scheduled outage Exceeding 7 hours duration | The allowable duration limit of power supply interruptions in a day due to planned outages. | Interruption shall not exceed 7 hours in a day, and supply should normally be restored by 6 pm. | 90 | % of complaints to redressed in time | 99.13 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Meter Complaint | Testing of Meter | Verifying the correctness of a meter at site when a consumer reports that the meter is not functioning properly. | Replace the meter within 15 days from the date of reporting by the consumer. | 90 | % of complaints to redressed in time | 96.82 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Meter Complaint | Replacement of stopped/defective/burned Meter | Replacing a consumer's meter that is detected or reported as stopped, damaged, or burnt. | Replace the meter within 24 hours in urban areas and 72 hours in rural areas from its detection or date of intimation by the consumer. | 90 | % of complaints to redressed in time | 98.69 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Meter Complaint | No-current complaint due to meter | Replacing a stopped, damaged, or burnt meter specifically when it causes a complete loss of supply (no current). | Replace the meter within 24 hours of reporting by the consumer or detection by the licensee (unless tempered, where it is replaced within 24 hours of consumer depositing security). | 90 | % of complaints to redressed in time | 99.51 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Shifting of Meters/Service Lines | Demand note | Inspecting and informing the consumer of the estimated cost of shifting meters or service lines. | Inspect and inform the estimated cost to the consumer ithin 15 days of receipt of application. | 90 | % of complaints to redressed in time | 98.8 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Shifting of Meters/Service Lines | Shifting of Meter | Shifting a consumer's meter after payment of the demand note and obtaining necessary clearances. | Shift the Meter for LT Consumers: Within 7 working days; HT & EHT Consumers: Within 15 working days from payment and clearance receipt. | 90 | % of complaints to redressed in time | 96.11 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Shifting of Meters/Service Lines | Shifting of Service line | Shifting a consumer's service line after payment of the demand note and obtaining necessary clearances. | Shift the service line for LT Consumers: Within 15 working days• HT Consumers: Within 1 month from payment and clearance receipt. | 90 | % of complaints to redressed in time | 98.45 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Release of New Connections or additional power | Release of new connection/additional power | Releasing new electricity connections or additional power to different categories of consumers. | Must be released as per the norms specified in the RERC (Supply Code & Connected Matters) Regulations, 2021. | 90 | % of complaints to redressed in time | 98.98 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Transfer of ownership or change of category | Transfer of ownership or change of category | Transferring the ownership of connection or changing the category of supply on the existing system. | Ownership of the connection or change of category on the existing system shall be transferred within 1 month from receipt of necessary documents certifying the transfer/change. | 90 | % of complaints to redressed in time | 97.96 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Disconnection of supply | Disconnection of supply | Disconnecting supply upon consumer request and clearance of dues. | Disconnect the supply in Class 1 Cities: Within 3 working days; Urban & Rural Areas: Within 7 working days from receipt of request and clearance. | 90 | % of complaints to redressed in time | 99.46 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Disconnection of supply | Issue of no dues certificate | Refunding security/money and issuing a "No-Dues Certificate" upon permanent disconnection. | Shall issue the certificate within 7 days from the date of disconnection or from the date of clearing the admissible dues, whichever is later. | 90 | % of complaints to redressed in time | 99.53 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Restoration of a Disconnected Consumer | Restoration of DC consumers | Restoring power supply to a disconnected (DC) consumer after they clear their dues. | Restore the supply within 6 working hours of clearing the dues (if infrastructure erection is required, as per RERC Supply Code Regulations, 2021). | 90 | % of complaints to redressed in time | 99.81 | % of complaints redressal in time | Yes | Yes | N/A
2024-25 | Delivery of Bills | Timely delivery of bills | Serving regular electricity bills on the consumers. | Served as per the timelines given in the RERC (Supply Code & Connected Matters) Regulations, 2021 (and within 7 days of written complaint if the first bill is delayed). | 90 | % of complaints to redressed in time | 99.51 | % of complaints redressal in time | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Restoration of Supply | No current complaints | Restoring supply in case of supply-related problems/faults like blowing of HT/LT fuse/MCB prior to meter or at distribution transformer or loose connections at meter/service line. | Restore the supply within Class 1 Cities: Within 2 hours; Urban Areas: Within 4 hours; Rural Areas: Within 8 hours from reporting. | 95 | % of complaints to redressed in time | 99.48 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Restoration of Supply | Overhead Line/ overhead Cable breakdowns | Restoring supply after overhead line or overhead cable breakdowns. | Restore the supply within Class 1 Cities: Within 4 hours; Urban Areas: Within 6 hours; Rural Areas: Within 10 hours from occurrence. | 90 | % of complaints to redressed in time | 99.5 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Restoration of Supply | Underground cable break down | Restoring supply in case of its underground cable breakdown. | Restore the supply within Class 1 Cities: Within 12 hours; Urban Areas: Within 12 hours; Rural Areas: Within 24 hours from occurrence. | 90 | % of complaints to redressed in time | 99.37 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Restoration of Supply | Scheduled outage Default in 24 hours notice | Giving consumers advance notification of scheduled outages or planned shutdowns. | Notification of planned shutdowns must be given at least 24 hours in advance (and on the same day in emergent cases). | 90 | % of complaints to redressed in time | 99.31 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Restoration of Supply | Scheduled outage Exceeding 7 hours duration | The allowable duration limit of power supply interruptions in a day due to planned outages. | Interruption shall not exceed 7 hours in a day, and supply should normally be restored by 6 pm. | 90 | % of complaints to redressed in time | 99.83 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Meter Complaint | Testing of Meter | Verifying the correctness of a meter at site when a consumer reports that the meter is not functioning properly. | Replace the meter within 15 days from the date of reporting by the consumer. | 90 | % of complaints to redressed in time | 99.49 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Meter Complaint | Replacement of stopped/defective/burned Meter | Replacing a consumer's meter that is detected or reported as stopped, damaged, or burnt. | Replace the meter within 24 hours in urban areas and 72 hours in rural areas from its detection or date of intimation by the consumer. | 90 | % of complaints to redressed in time | 99.16 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Meter Complaint | No-current complaint due to meter | Replacing a stopped, damaged, or burnt meter specifically when it causes a complete loss of supply (no current). | Replace the meter within 24 hours of reporting by the consumer or detection by the licensee (unless tempered, where it is replaced within 24 hours of consumer depositing security). | 90 | % of complaints to redressed in time | 99.52 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Shifting of Meters/Service Lines | Demand note | Inspecting and informing the consumer of the estimated cost of shifting meters or service lines. | Inspect and inform the estimated cost to the consumer ithin 15 days of receipt of application. | 90 | % of complaints to redressed in time | 99.56 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Shifting of Meters/Service Lines | Shifting of Meter | Shifting a consumer's meter after payment of the demand note and obtaining necessary clearances. | Shift the Meter for LT Consumers: Within 7 working days; HT & EHT Consumers: Within 15 working days from payment and clearance receipt. | 90 | % of complaints to redressed in time | 99.66 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Shifting of Meters/Service Lines | Shifting of Service line | Shifting a consumer's service line after payment of the demand note and obtaining necessary clearances. | Shift the service line for LT Consumers: Within 15 working days• HT Consumers: Within 1 month from payment and clearance receipt. | 90 | % of complaints to redressed in time | 99.56 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Release of New Connections or additional power | Release of new connection/additional power | Releasing new electricity connections or additional power to different categories of consumers. | Must be released as per the norms specified in the RERC (Supply Code & Connected Matters) Regulations, 2021. | 90 | % of complaints to redressed in time | 99.59 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Transfer of ownership or change of category | Transfer of ownership or change of category | Transferring the ownership of connection or changing the category of supply on the existing system. | Ownership of the connection or change of category on the existing system shall be transferred within 1 month from receipt of necessary documents certifying the transfer/change. | 90 | % of complaints to redressed in time | 99.43 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Disconnection of supply | Disconnection of supply | Disconnecting supply upon consumer request and clearance of dues. | Disconnect the supply in Class 1 Cities: Within 3 working days; Urban & Rural Areas: Within 7 working days from receipt of request and clearance. | 90 | % of complaints to redressed in time | 99.76 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Disconnection of supply | Issue of no dues certificate | Refunding security/money and issuing a "No-Dues Certificate" upon permanent disconnection. | Shall issue the certificate within 7 days from the date of disconnection or from the date of clearing the admissible dues, whichever is later. | 90 | % of complaints to redressed in time | 99.99 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Restoration of a Disconnected Consumer | Restoration of DC consumers | Restoring power supply to a disconnected (DC) consumer after they clear their dues. | Restore the supply within 6 working hours of clearing the dues (if infrastructure erection is required, as per RERC Supply Code Regulations, 2021). | 90 | % of complaints to redressed in time | 99.8 | % of complaints redressal in time | Yes | Yes | N/A
2025-26 | Delivery of Bills | Timely delivery of bills | Serving regular electricity bills on the consumers. | Served as per the timelines given in the RERC (Supply Code & Connected Matters) Regulations, 2021 (and within 7 days of written complaint if the first bill is delayed). | 90 | % of complaints to redressed in time | 99.98 | % of complaints redressal in time | Yes | Yes | N/A

## JdVVNL,RAJASTHAN
Jodhpur Vidyut Vitran Nigam Limited
RERC ( Standards of Performance for Distribution Licensees) Regulations, 2021 | State that the RERC (Standards of Performance for Distribution Licensees) Regulations, 2021 came into force on 15 Apr 2021. It applies from 15 Apr 2021 onward; FY 2021-22 therefore starts before the regulation came into force.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Restoration of Supply | No current complaints | Restoring supply in case of supply-related problems/faults like blowing of HT/LT fuse/MCB prior to meter or at distribution transformer or loose connections at meter/service line. | Restore the supply within Class 1 Cities: Within 2 hours; Urban Areas: Within 4 hours; Rural Areas: Within 8 hours from reporting. | 95 | % of complaints to be redressed in time | 97.74 | % of complaints redressed in time | Yes | Yes | N/A
2021-22 | Restoration of Supply | Overhead Line/ overhead Cable breakdowns | Restoring supply after overhead line or overhead cable breakdowns. | Restore the supply within Class 1 Cities: Within 4 hours; Urban Areas: Within 6 hours; Rural Areas: Within 10 hours from occurrence. | 90 | % of complaints to be redressed in time | 98.81 | % of complaints redressed in time | Yes | Yes | N/A
2021-22 | Restoration of Supply | Underground cable break down | Restoring supply in case of its underground cable breakdown. | Restore the supply within Class 1 Cities: Within 12 hours; Urban Areas: Within 12 hours; Rural Areas: Within 24 hours from occurrence. | 90 | % of complaints to be redressed in time | 97.85 | % of complaints redressed in time | Yes | Yes | N/A
2021-22 | Restoration of Supply | Scheduled outage Default in 24 hours notice | Giving consumers advance notification of scheduled outages or planned shutdowns. | Notification of planned shutdowns must be given at least 24 hours in advance (and on the same day in emergent cases). | 90 | % of complaints to be redressed in time | 98.87 | % of complaints redressed in time | Yes | Yes | N/A
2021-22 | Restoration of Supply | Scheduled outage Exceeding 7 hours duration | The allowable duration limit of power supply interruptions in a day due to planned outages. | Interruption shall not exceed 7 hours in a day, and supply should normally be restored by 6 pm. | 90 | % of complaints to be redressed in time | 99.89 | % of complaints redressed in time | Yes | Yes | N/A
2021-22 | Meter Complaint | Testing of Meter | Verifying the correctness of a meter at site when a consumer reports that the meter is not functioning properly. | Replace the meter within 15 days from the date of reporting by the consumer. | 90 | % of complaints to be redressed in time | 98.74 | % of complaints redressed in time | Yes | Yes | N/A
2021-22 | Meter Complaint | Replacement of stopped/defective/burned Meter | Replacing a consumer's meter that is detected or reported as stopped, damaged, or burnt. | Replace the meter within 24 hours in urban areas and 72 hours in rural areas from its detection or date of intimation by the consumer. | 90 | % of complaints to be redressed in time | 97.18 | % of complaints redressed in time | Yes | Yes | N/A
2021-22 | Meter Complaint | No-current complaint due to meter | Replacing a stopped, damaged, or burnt meter specifically when it causes a complete loss of supply (no current). | Replace the meter within 24 hours of reporting by the consumer or detection by the licensee (unless tempered, where it is replaced within 24 hours of consumer depositing security). | 90 | % of complaints to be redressed in time | 97.53 | % of complaints redressed in time | Yes | Yes | N/A
2021-22 | Shifting of Meters/Service Lines | Demand note | Inspecting and informing the consumer of the estimated cost of shifting meters or service lines. | Inspect and inform the estimated cost to the consumer ithin 15 days of receipt of application. | 90 | % of complaints to be redressed in time | 96.82 | % of complaints redressed in time | Yes | Yes | N/A
2021-22 | Shifting of Meters/Service Lines | Shifting of Meter | Shifting a consumer's meter after payment of the demand note and obtaining necessary clearances. | Shift the Meter for LT Consumers: Within 7 working days; HT & EHT Consumers: Within 15 working days from payment and clearance receipt. | 90 | % of complaints to be redressed in time | 97.89 | % of complaints redressed in time | Yes | Yes | N/A
2021-22 | Shifting of Meters/Service Lines | Shifting of Service line | Shifting a consumer's service line after payment of the demand note and obtaining necessary clearances. | Shift the service line for LT Consumers: Within 15 working days• HT Consumers: Within 1 month from payment and clearance receipt. | 90 | % of complaints to be redressed in time | 98.29 | % of complaints redressed in time | Yes | Yes | N/A
2021-22 | Release of New Connections or additional power | Release of new connection/additional power | Releasing new electricity connections or additional power to different categories of consumers. | Must be released as per the norms specified in the RERC (Supply Code & Connected Matters) Regulations, 2021. | 90 | % of complaints to be redressed in time | 98.22 | % of complaints redressed in time | Yes | Yes | N/A
2021-22 | Transfer of ownership or change of category | Transfer of ownership or change of category | Transferring the ownership of connection or changing the category of supply on the existing system. | Ownership of the connection or change of category on the existing system shall be transferred within 1 month from receipt of necessary documents certifying the transfer/change. | 90 | % of complaints to be redressed in time | 98.21 | % of complaints redressed in time | Yes | Yes | N/A
2021-22 | Disconnection of supply | Disconnection of supply | Disconnecting supply upon consumer request and clearance of dues. | Disconnect the supply in Class 1 Cities: Within 3 working days; Urban & Rural Areas: Within 7 working days from receipt of request and clearance. | 90 | % of complaints to be redressed in time | 98.69 | % of complaints redressed in time | Yes | Yes | N/A
2021-22 | Disconnection of supply | Issue of no dues certificate | Refunding security/money and issuing a "No-Dues Certificate" upon permanent disconnection. | Shall issue the certificate within 7 days from the date of disconnection or from the date of clearing the admissible dues, whichever is later. | 90 | % of complaints to be redressed in time | 99.02 | % of complaints redressed in time | Yes | Yes | N/A
2021-22 | Restoration of a Disconnected Consumer | Restoration of DC consumers | Restoring power supply to a disconnected (DC) consumer after they clear their dues. | Restore the supply within 6 working hours of clearing the dues (if infrastructure erection is required, as per RERC Supply Code Regulations, 2021). | 90 | % of complaints to be redressed in time | 99.11 | % of complaints redressed in time | Yes | Yes | N/A
2021-22 | Delivery of Bills | Timely delivery of bills | Serving regular electricity bills on the consumers. | Served as per the timelines given in the RERC (Supply Code & Connected Matters) Regulations, 2021 (and within 7 days of written complaint if the first bill is delayed). | 90 | % of complaints to be redressed in time | 97.23 | % of complaints redressed in time | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Restoration of Supply | No current complaints | Restoring supply in case of supply-related problems/faults like blowing of HT/LT fuse/MCB prior to meter or at distribution transformer or loose connections at meter/service line. | Restore the supply within Class 1 Cities: Within 2 hours; Urban Areas: Within 4 hours; Rural Areas: Within 8 hours from reporting. | 95 | % of complaints to be redressed in time | 97.87 | % of complaints redressed in time | Yes | Yes | N/A
2022-23 | Restoration of Supply | Overhead Line/ overhead Cable breakdowns | Restoring supply after overhead line or overhead cable breakdowns. | Restore the supply within Class 1 Cities: Within 4 hours; Urban Areas: Within 6 hours; Rural Areas: Within 10 hours from occurrence. | 90 | % of complaints to be redressed in time | 97.43 | % of complaints redressed in time | Yes | Yes | N/A
2022-23 | Restoration of Supply | Underground cable break down | Restoring supply in case of its underground cable breakdown. | Restore the supply within Class 1 Cities: Within 12 hours; Urban Areas: Within 12 hours; Rural Areas: Within 24 hours from occurrence. | 90 | % of complaints to be redressed in time | 97.78 | % of complaints redressed in time | Yes | Yes | N/A
2022-23 | Restoration of Supply | Scheduled outage Default in 24 hours notice | Giving consumers advance notification of scheduled outages or planned shutdowns. | Notification of planned shutdowns must be given at least 24 hours in advance (and on the same day in emergent cases). | 90 | % of complaints to be redressed in time | 98.59 | % of complaints redressed in time | Yes | Yes | N/A
2022-23 | Restoration of Supply | Scheduled outage Exceeding 7 hours duration | The allowable duration limit of power supply interruptions in a day due to planned outages. | Interruption shall not exceed 7 hours in a day, and supply should normally be restored by 6 pm. | 90 | % of complaints to be redressed in time | 99.73 | % of complaints redressed in time | Yes | Yes | N/A
2022-23 | Meter Complaint | Testing of Meter | Verifying the correctness of a meter at site when a consumer reports that the meter is not functioning properly. | Replace the meter within 15 days from the date of reporting by the consumer. | 90 | % of complaints to be redressed in time | 97.94 | % of complaints redressed in time | Yes | Yes | N/A
2022-23 | Meter Complaint | Replacement of stopped/defective/burned Meter | Replacing a consumer's meter that is detected or reported as stopped, damaged, or burnt. | Replace the meter within 24 hours in urban areas and 72 hours in rural areas from its detection or date of intimation by the consumer. | 90 | % of complaints to be redressed in time | 96.88 | % of complaints redressed in time | Yes | Yes | N/A
2022-23 | Meter Complaint | No-current complaint due to meter | Replacing a stopped, damaged, or burnt meter specifically when it causes a complete loss of supply (no current). | Replace the meter within 24 hours of reporting by the consumer or detection by the licensee (unless tempered, where it is replaced within 24 hours of consumer depositing security). | 90 | % of complaints to be redressed in time | 95.07 | % of complaints redressed in time | Yes | Yes | N/A
2022-23 | Shifting of Meters/Service Lines | Demand note | Inspecting and informing the consumer of the estimated cost of shifting meters or service lines. | Inspect and inform the estimated cost to the consumer ithin 15 days of receipt of application. | 90 | % of complaints to be redressed in time | 95.4 | % of complaints redressed in time | Yes | Yes | N/A
2022-23 | Shifting of Meters/Service Lines | Shifting of Meter | Shifting a consumer's meter after payment of the demand note and obtaining necessary clearances. | Shift the Meter for LT Consumers: Within 7 working days; HT & EHT Consumers: Within 15 working days from payment and clearance receipt. | 90 | % of complaints to be redressed in time | 97.98 | % of complaints redressed in time | Yes | Yes | N/A
2022-23 | Shifting of Meters/Service Lines | Shifting of Service line | Shifting a consumer's service line after payment of the demand note and obtaining necessary clearances. | Shift the service line for LT Consumers: Within 15 working days; HT Consumers: Within 1 month from payment and clearance receipt. | 90 | % of complaints to be redressed in time | 98.36 | % of complaints redressed in time | Yes | Yes | N/A
2022-23 | Release of New Connections or additional power | Release of new connection/additional power | Releasing new electricity connections or additional power to different categories of consumers. | Must be released as per the norms specified in the RERC (Supply Code & Connected Matters) Regulations, 2021. | 90 | % of complaints to be redressed in time | 98.94 | % of complaints redressed in time | Yes | Yes | N/A
2022-23 | Transfer of ownership or change of category | Transfer of ownership or change of category | Transferring the ownership of connection or changing the category of supply on the existing system. | Ownership of the connection or change of category on the existing system shall be transferred within 1 month from receipt of necessary documents certifying the transfer/change. | 90 | % of complaints to be redressed in time | 98.95 | % of complaints redressed in time | Yes | Yes | N/A
2022-23 | Disconnection of supply | Disconnection of supply | Disconnecting supply upon consumer request and clearance of dues. | Disconnect the supply in Class 1 Cities: Within 3 working days; Urban & Rural Areas: Within 7 working days from receipt of request and clearance. | 90 | % of complaints to be redressed in time | 98.96 | % of complaints redressed in time | Yes | Yes | N/A
2022-23 | Disconnection of supply | Issue of no dues certificate | Refunding security/money and issuing a "No-Dues Certificate" upon permanent disconnection. | Shall issue the certificate within 7 days from the date of disconnection or from the date of clearing the admissible dues, whichever is later. | 90 | % of complaints to be redressed in time | 96.28 | % of complaints redressed in time | Yes | Yes | N/A
2022-23 | Restoration of a Disconnected Consumer | Restoration of DC consumers | Restoring power supply to a disconnected (DC) consumer after they clear their dues. | Restore the supply within 6 working hours of clearing the dues. | 90 | % of complaints to be redressed in time | 94.99 | % of complaints redressed in time | Yes | Yes | N/A
2022-23 | Delivery of Bills | Timely delivery of bills | Serving regular electricity bills on the consumers. | Served as per the timelines given in the RERC (Supply Code & Connected Matters) Regulations, 2021 (and within 7 days of written complaint if the first bill is delayed). | 90 | % of complaints to be redressed in time | 97.96 | % of complaints redressed in time | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Restoration of Supply | No current complaints | Restoring supply in case of supply-related problems/faults like blowing of HT/LT fuse/MCB prior to meter or at distribution transformer or loose connections at meter/service line. | Restore the supply within Class 1 Cities: Within 2 hours; Urban Areas: Within 4 hours; Rural Areas: Within 8 hours from reporting. | 95 | % of complaints to be redressed in time | 99.15 | % of complaints redressed in time | Yes | Yes | N/A
2023-24 | Restoration of Supply | Overhead Line/ overhead Cable breakdowns | Restoring supply after overhead line or overhead cable breakdowns. | Restore the supply within Class 1 Cities: Within 4 hours; Urban Areas: Within 6 hours; Rural Areas: Within 10 hours from occurrence. | 90 | % of complaints to be redressed in time | 94.15 | % of complaints redressed in time | Yes | Yes | N/A
2023-24 | Restoration of Supply | Underground cable break down | Restoring supply in case of its underground cable breakdown. | Restore the supply within Class 1 Cities: Within 12 hours; Urban Areas: Within 12 hours; Rural Areas: Within 24 hours from occurrence. | 90 | % of complaints to be redressed in time | 100 | % of complaints redressed in time | Yes | Yes | N/A
2023-24 | Restoration of Supply | Scheduled outage Default in 24 hours notice | Giving consumers advance notification of scheduled outages or planned shutdowns. | Notification of planned shutdowns must be given at least 24 hours in advance (and on the same day in emergent cases). | 90 | % of complaints to be redressed in time | 95.91 | % of complaints redressed in time | Yes | Yes | N/A
2023-24 | Restoration of Supply | Scheduled outage Exceeding 7 hours duration | The allowable duration limit of power supply interruptions in a day due to planned outages. | Interruption shall not exceed 7 hours in a day, and supply should normally be restored by 6 pm. | 90 | % of complaints to be redressed in time | 95.52 | % of complaints redressed in time | Yes | Yes | N/A
2023-24 | Meter Complaint | Testing of Meter | Verifying the correctness of a meter at site when a consumer reports that the meter is not functioning properly. | Replace the meter within 15 days from the date of reporting by the consumer. | 90 | % of complaints to be redressed in time | 96.15 | % of complaints redressed in time | Yes | Yes | N/A
2023-24 | Meter Complaint | Replacement of stopped/defective/burned Meter | Replacing a consumer's meter that is detected or reported as stopped, damaged, or burnt. | Replace the meter within 24 hours in urban areas and 72 hours in rural areas from its detection or date of intimation by the consumer. | 90 | % of complaints to be redressed in time | 93.29 | % of complaints redressed in time | Yes | Yes | N/A
2023-24 | Meter Complaint | No-current complaint due to meter | Replacing a stopped, damaged, or burnt meter specifically when it causes a complete loss of supply (no current). | Replace the meter within 24 hours of reporting by the consumer or detection by the licensee (unless tempered, where it is replaced within 24 hours of consumer depositing security). | 90 | % of complaints to be redressed in time | 96.9 | % of complaints redressed in time | Yes | Yes | N/A
2023-24 | Shifting of Meters/Service Lines | Demand note | Inspecting and informing the consumer of the estimated cost of shifting meters or service lines. | Inspect and inform the estimated cost to the consumer ithin 15 days of receipt of application. | 90 | % of complaints to be redressed in time | 98.85 | % of complaints redressed in time | Yes | Yes | N/A
2023-24 | Shifting of Meters/Service Lines | Shifting of Meter | Shifting a consumer's meter after payment of the demand note and obtaining necessary clearances. | Shift the Meter for LT Consumers: Within 7 working days; HT & EHT Consumers: Within 15 working days from payment and clearance receipt. | 90 | % of complaints to be redressed in time | 95.8 | % of complaints redressed in time | Yes | Yes | N/A
2023-24 | Shifting of Meters/Service Lines | Shifting of Service line | Shifting a consumer's service line after payment of the demand note and obtaining necessary clearances. | Shift the service line for LT Consumers: Within 15 working days• HT Consumers: Within 1 month from payment and clearance receipt. | 90 | % of complaints to be redressed in time | 98.54 | % of complaints redressed in time | Yes | Yes | N/A
2023-24 | Release of New Connections or additional power | Release of new connection/additional power | Releasing new electricity connections or additional power to different categories of consumers. | Must be released as per the norms specified in the RERC (Supply Code & Connected Matters) Regulations, 2021. | 90 | % of complaints to be redressed in time | 99.33 | % of complaints redressed in time | Yes | Yes | N/A
2023-24 | Transfer of ownership or change of category | Transfer of ownership or change of category | Transferring the ownership of connection or changing the category of supply on the existing system. | Ownership of the connection or change of category on the existing system shall be transferred within 1 month from receipt of necessary documents certifying the transfer/change. | 90 | % of complaints to be redressed in time | 96.98 | % of complaints redressed in time | Yes | Yes | N/A
2023-24 | Disconnection of supply | Disconnection of supply | Disconnecting supply upon consumer request and clearance of dues. | Disconnect the supply in Class 1 Cities: Within 3 working days; Urban & Rural Areas: Within 7 working days from receipt of request and clearance. | 90 | % of complaints to be redressed in time | 99.97 | % of complaints redressed in time | Yes | Yes | N/A
2023-24 | Disconnection of supply | Issue of no dues certificate | Refunding security/money and issuing a "No-Dues Certificate" upon permanent disconnection. | Shall issue the certificate within 7 days from the date of disconnection or from the date of clearing the admissible dues, whichever is later. | 90 | % of complaints to be redressed in time | 97.52 | % of complaints redressed in time | Yes | Yes | N/A
2023-24 | Restoration of a Disconnected Consumer | Restoration of DC consumers | Restoring power supply to a disconnected (DC) consumer after they clear their dues. | Restore the supply within 6 working hours of clearing the dues (if infrastructure erection is required, as per RERC Supply Code Regulations, 2021). | 90 | % of complaints to be redressed in time | 93.78 | % of complaints redressed in time | Yes | Yes | N/A
2023-24 | Delivery of Bills | Timely delivery of bills | Serving regular electricity bills on the consumers. | Served as per the timelines given in the RERC (Supply Code & Connected Matters) Regulations, 2021 (and within 7 days of written complaint if the first bill is delayed). | 90 | % of complaints to be redressed in time | 98.5 | % of complaints redressed in time | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Restoration of Supply | No current complaints | Restoring supply in case of supply-related problems/faults like blowing of HT/LT fuse/MCB prior to meter or at distribution transformer or loose connections at meter/service line. | Restore the supply within Class 1 Cities: Within 2 hours; Urban Areas: Within 4 hours; Rural Areas: Within 8 hours from reporting. | 95 | % of complaints to be redressed in time | 98.48 | % of complaints redressed in time | Yes | Yes | N/A
2024-25 | Restoration of Supply | Overhead Line/ overhead Cable breakdowns | Restoring supply after overhead line or overhead cable breakdowns. | Restore the supply within Class 1 Cities: Within 4 hours; Urban Areas: Within 6 hours; Rural Areas: Within 10 hours from occurrence. | 90 | % of complaints to be redressed in time | 97.52 | % of complaints redressed in time | Yes | Yes | N/A
2024-25 | Restoration of Supply | Underground cable break down | Restoring supply in case of its underground cable breakdown. | Restore the supply within Class 1 Cities: Within 12 hours; Urban Areas: Within 12 hours; Rural Areas: Within 24 hours from occurrence. | 90 | % of complaints to be redressed in time | 98.21 | % of complaints redressed in time | Yes | Yes | N/A
2024-25 | Restoration of Supply | Scheduled outage Default in 24 hours notice | Giving consumers advance notification of scheduled outages or planned shutdowns. | Notification of planned shutdowns must be given at least 24 hours in advance (and on the same day in emergent cases). | 90 | % of complaints to be redressed in time | 97.02 | % of complaints redressed in time | Yes | Yes | N/A
2024-25 | Restoration of Supply | Scheduled outage Exceeding 7 hours duration | The allowable duration limit of power supply interruptions in a day due to planned outages. | Interruption shall not exceed 7 hours in a day, and supply should normally be restored by 6 pm. | 90 | % of complaints to be redressed in time | 100 | % of complaints redressed in time | Yes | Yes | N/A
2024-25 | Meter Complaint | Testing of Meter | Verifying the correctness of a meter at site when a consumer reports that the meter is not functioning properly. | Replace the meter within 15 days from the date of reporting by the consumer. | 90 | % of complaints to be redressed in time | 94.01 | % of complaints redressed in time | Yes | Yes | N/A
2024-25 | Meter Complaint | Replacement of stopped/defective/burned Meter | Replacing a consumer's meter that is detected or reported as stopped, damaged, or burnt. | Replace the meter within 24 hours in urban areas and 72 hours in rural areas from its detection or date of intimation by the consumer. | 90 | % of complaints to be redressed in time | 92.29 | % of complaints redressed in time | Yes | Yes | N/A
2024-25 | Meter Complaint | No-current complaint due to meter | Replacing a stopped, damaged, or burnt meter specifically when it causes a complete loss of supply (no current). | Replace the meter within 24 hours of reporting by the consumer or detection by the licensee (unless tempered, where it is replaced within 24 hours of consumer depositing security). | 90 | % of complaints to be redressed in time | 81.83 | % of complaints redressed in time | Yes | No | N/A
2024-25 | Shifting of Meters/Service Lines | Demand note | Inspecting and informing the consumer of the estimated cost of shifting meters or service lines. | Inspect and inform the estimated cost to the consumer ithin 15 days of receipt of application. | 90 | % of complaints to be redressed in time | 99.25 | % of complaints redressed in time | Yes | Yes | N/A
2024-25 | Shifting of Meters/Service Lines | Shifting of Meter | Shifting a consumer's meter after payment of the demand note and obtaining necessary clearances. | Shift the Meter for LT Consumers: Within 7 working days; HT & EHT Consumers: Within 15 working days from payment and clearance receipt. | 90 | % of complaints to be redressed in time | 99.29 | % of complaints redressed in time | Yes | Yes | N/A
2024-25 | Shifting of Meters/Service Lines | Shifting of Service line | Shifting a consumer's service line after payment of the demand note and obtaining necessary clearances. | Shift the service line for LT Consumers: Within 15 working days• HT Consumers: Within 1 month from payment and clearance receipt. | 90 | % of complaints to be redressed in time | 98.49 | % of complaints redressed in time | Yes | Yes | N/A
2024-25 | Release of New Connections or additional power | Release of new connection/additional power | Releasing new electricity connections or additional power to different categories of consumers. | Must be released as per the norms specified in the RERC (Supply Code & Connected Matters) Regulations, 2021. | 90 | % of complaints to be redressed in time | 98.94 | % of complaints redressed in time | Yes | Yes | N/A
2024-25 | Transfer of ownership or change of category | Transfer of ownership or change of category | Transferring the ownership of connection or changing the category of supply on the existing system. | Ownership of the connection or change of category on the existing system shall be transferred within 1 month from receipt of necessary documents certifying the transfer/change. | 90 | % of complaints to be redressed in time | 99.52 | % of complaints redressed in time | Yes | Yes | N/A
2024-25 | Disconnection of supply | Disconnection of supply | Disconnecting supply upon consumer request and clearance of dues. | Disconnect the supply in Class 1 Cities: Within 3 working days; Urban & Rural Areas: Within 7 working days from receipt of request and clearance. | 90 | % of complaints to be redressed in time | 99.86 | % of complaints redressed in time | Yes | Yes | N/A
2024-25 | Disconnection of supply | Issue of no dues certificate | Refunding security/money and issuing a "No-Dues Certificate" upon permanent disconnection. | Shall issue the certificate within 7 days from the date of disconnection or from the date of clearing the admissible dues, whichever is later. | 90 | % of complaints to be redressed in time | 99.7 | % of complaints redressed in time | Yes | Yes | N/A
2024-25 | Restoration of a Disconnected Consumer | Restoration of DC consumers | Restoring power supply to a disconnected (DC) consumer after they clear their dues. | Restore the supply within 6 working hours of clearing the dues (if infrastructure erection is required, as per RERC Supply Code Regulations, 2021). | 90 | % of complaints to be redressed in time | 99.88 | % of complaints redressed in time | Yes | Yes | N/A
2024-25 | Delivery of Bills | Timely delivery of bills | Serving regular electricity bills on the consumers. | Served as per the timelines given in the RERC (Supply Code & Connected Matters) Regulations, 2021 (and within 7 days of written complaint if the first bill is delayed). | 90 | % of complaints to be redressed in time | 88.36 | % of complaints redressed in time | Yes | No | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Restoration of Supply | No current complaints | Restoring supply in case of supply-related problems/faults like blowing of HT/LT fuse/MCB prior to meter or at distribution transformer or loose connections at meter/service line. | Restore the supply within Class 1 Cities: Within 2 hours; Urban Areas: Within 4 hours; Rural Areas: Within 8 hours from reporting. | 95 | % of complaints to be redressed in time | 98.75 | % of complaints redressed in time | Yes | Yes | N/A
2025-26 | Restoration of Supply | Overhead Line/ overhead Cable breakdowns | Restoring supply after overhead line or overhead cable breakdowns. | Restore the supply within Class 1 Cities: Within 4 hours; Urban Areas: Within 6 hours; Rural Areas: Within 10 hours from occurrence. | 90 | % of complaints to be redressed in time | 99 | % of complaints redressed in time | Yes | Yes | N/A
2025-26 | Restoration of Supply | Underground cable break down | Restoring supply in case of its underground cable breakdown. | Restore the supply within Class 1 Cities: Within 12 hours; Urban Areas: Within 12 hours; Rural Areas: Within 24 hours from occurrence. | 90 | % of complaints to be redressed in time | 98.75 | % of complaints redressed in time | Yes | Yes | N/A
2025-26 | Restoration of Supply | Scheduled outage Default in 24 hours notice | Giving consumers advance notification of scheduled outages or planned shutdowns. | Notification of planned shutdowns must be given at least 24 hours in advance (and on the same day in emergent cases). | 90 | % of complaints to be redressed in time | 100 | % of complaints redressed in time | Yes | Yes | N/A
2025-26 | Restoration of Supply | Scheduled outage Exceeding 7 hours duration | The allowable duration limit of power supply interruptions in a day due to planned outages. | Interruption shall not exceed 7 hours in a day, and supply should normally be restored by 6 pm. | 90 | % of complaints to be redressed in time | 100 | % of complaints redressed in time | Yes | Yes | N/A
2025-26 | Meter Complaint | Testing of Meter | Verifying the correctness of a meter at site when a consumer reports that the meter is not functioning properly. | Replace the meter within 15 days from the date of reporting by the consumer. | 90 | % of complaints to be redressed in time | 98.5 | % of complaints redressed in time | Yes | Yes | N/A
2025-26 | Meter Complaint | Replacement of stopped/defective/burned Meter | Replacing a consumer's meter that is detected or reported as stopped, damaged, or burnt. | Replace the meter within 24 hours in urban areas and 72 hours in rural areas from its detection or date of intimation by the consumer. | 90 | % of complaints to be redressed in time | 99 | % of complaints redressed in time | Yes | Yes | N/A
2025-26 | Meter Complaint | No-current complaint due to meter | Replacing a stopped, damaged, or burnt meter specifically when it causes a complete loss of supply (no current). | Replace the meter within 24 hours of reporting by the consumer or detection by the licensee (unless tempered, where it is replaced within 24 hours of consumer depositing security). | 90 | % of complaints to be redressed in time | 99.75 | % of complaints redressed in time | Yes | Yes | N/A
2025-26 | Shifting of Meters/Service Lines | Demand note | Inspecting and informing the consumer of the estimated cost of shifting meters or service lines. | Inspect and inform the estimated cost to the consumer ithin 15 days of receipt of application. | 90 | % of complaints to be redressed in time | 99.75 | % of complaints redressed in time | Yes | Yes | N/A
2025-26 | Shifting of Meters/Service Lines | Shifting of Meter | Shifting a consumer's meter after payment of the demand note and obtaining necessary clearances. | Shift the Meter for LT Consumers: Within 7 working days; HT & EHT Consumers: Within 15 working days from payment and clearance receipt. | 90 | % of complaints to be redressed in time | 99.75 | % of complaints redressed in time | Yes | Yes | N/A
2025-26 | Shifting of Meters/Service Lines | Shifting of Service line | Shifting a consumer's service line after payment of the demand note and obtaining necessary clearances. | Shift the service line for LT Consumers: Within 15 working days• HT Consumers: Within 1 month from payment and clearance receipt. | 90 | % of complaints to be redressed in time | 89 | % of complaints redressed in time | Yes | No | N/A
2025-26 | Release of New Connections or additional power | Release of new connection/additional power | Releasing new electricity connections or additional power to different categories of consumers. | Must be released as per the norms specified in the RERC (Supply Code & Connected Matters) Regulations, 2021. | 90 | % of complaints to be redressed in time | 100 | % of complaints redressed in time | Yes | Yes | N/A
2025-26 | Transfer of ownership or change of category | Transfer of ownership or change of category | Transferring the ownership of connection or changing the category of supply on the existing system. | Ownership of the connection or change of category on the existing system shall be transferred within 1 month from receipt of necessary documents certifying the transfer/change. | 90 | % of complaints to be redressed in time | 100 | % of complaints redressed in time | Yes | Yes | N/A
2025-26 | Disconnection of supply | Disconnection of supply | Disconnecting supply upon consumer request and clearance of dues. | Disconnect the supply in Class 1 Cities: Within 3 working days; Urban & Rural Areas: Within 7 working days from receipt of request and clearance. | 90 | % of complaints to be redressed in time | 99.75 | % of complaints redressed in time | Yes | Yes | N/A
2025-26 | Disconnection of supply | Issue of no dues certificate | Refunding security/money and issuing a "No-Dues Certificate" upon permanent disconnection. | Shall issue the certificate within 7 days from the date of disconnection or from the date of clearing the admissible dues, whichever is later. | 90 | % of complaints to be redressed in time | 100 | % of complaints redressed in time | Yes | Yes | N/A
2025-26 | Restoration of a Disconnected Consumer | Restoration of DC consumers | Restoring power supply to a disconnected (DC) consumer after they clear their dues. | Restore the supply within 6 working hours of clearing the dues (if infrastructure erection is required, as per RERC Supply Code Regulations, 2021). | 90 | % of complaints to be redressed in time | 100 | % of complaints redressed in time | Yes | Yes | N/A
2025-26 | Delivery of Bills | Timely delivery of bills | Serving regular electricity bills on the consumers. | Served as per the timelines given in the RERC (Supply Code & Connected Matters) Regulations, 2021 (and within 7 days of written complaint if the first bill is delayed). | 90 | % of complaints to be redressed in time | 97.5 | % of complaints redressed in time | Yes | Yes | N/A

## NBPDCL,BIHAR
North Bihar Power Distribution Company Limited
Bihar Electricity Regulatory Commission (Standards of Performance of Distribution Licensee) Regulations, 2006 | Bihar Electricity Regulatory Commission (Standards of Performance of Distribution Licensee) (First Amendment) Regulations, 2012 | Bihar Electricity Regulatory Commission (Standards of Performance of Distribution Licensee) (First Amendment) Regulations, 2017
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Restoration of Power Supply | Normal Fuse-off Calls (Urban) | Replacing blown Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | The distribution licensee must replace blown fuses and restore power supply within 4 hours in cities and towns. | 95 | At least 95% of calls received must be rectified within the specified time limit. | N/A | No | N/A | Reported data not available.
2021-22 | Restoration of Power Supply | Normal Fuse-off Calls (Rural) | Replacing blown Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | In rural areas, the licensee is mandated to replace blown fuses and restore the supply within 24 hours. | 95 | At least 95% of calls received must be rectified within the specified time limit. | N/A | No | N/A | Reported data not available.
2021-22 | Restoration of Power Supply | Overhead Line / Cable Breakdowns (Urban) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | For overhead line or cable failures in cities and towns, the utility must resolve the breakdown and restore electricity within 6 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2021-22 | Restoration of Power Supply | Overhead Line / Cable Breakdowns (Rural) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | Power supply restoration following an overhead line or cable breakdown in rural areas must be completed within 36 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2021-22 | Restoration of Power Supply | Underground Cable Breakdowns (Urban) | Locating, repairing, and re-energising the system following faults in underground cables. | The licensee is required to locate, repair, and re-energize the network within 24 hours of an underground cable fault in urban areas. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2021-22 | Restoration of Power Supply | Underground Cable Breakdowns (Rural) | Locating, repairing, and re-energising the system following faults in underground cables. | Underground cable faults in rural areas must be located and fully repaired to restore supply within 48 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2021-22 | Restoration of Power Supply | Distribution Transformer Failure (Urban) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | The utility must replace or repair a failed distribution transformer and restore supply to consumers within 24 hours in urban areas. | 95 | At least 95% of failed transformers must be replaced within the specified time limit. | N/A | No | N/A | Reported data not available.
2021-22 | Restoration of Power Supply | Distribution Transformer Failure (Rural) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | Following a distribution transformer failure in rural areas, the company must complete replacement and restore supply within 72 hours. | 95 | At least 95% of failed transformers must be replaced within the specified time limit. | N/A | No | N/A | Reported data not available.
2021-22 | System Outages | Scheduled Outages (Duration) | Pre-arranged shut-downs of equipment and lines for necessary maintenance work. | The maximum duration of a pre-planned maintenance outage is strictly capped at 12 hours in a single stretch. | 95 | At least 95% of scheduled outages must comply with the maximum duration standard. | N/A | No | N/A | Reported data not available.
2021-22 | System Outages | Scheduled Outages (Restoration) | Pre-arranged shut-downs of equipment and lines for necessary maintenance work. | During pre-arranged maintenance, the utility must ensure power supply is fully restored not later than 6:00 PM. | 95 | At least 95% of planned outages must have supply restored by 6:00 PM. | N/A | No | N/A | Reported data not available.
2021-22 | Street Light Complaints | Street Light Faults | Rectification of line faults and replacement of public street lighting fixtures. | The licensee must rectify line faults or replace fused and defective public street lighting fixtures as soon as possible. | 90 | At least 90% of street light complaints must be resolved. | N/A | No | N/A | Reported data not available.
2021-22 | Billing Complaints | Billing Accuracy | Total allowable rate of billing errors across all prepared accounts. | The total number of billing mistakes across all processed accounts must be kept under a maximum limit of 1% of total bills prepared. | 1% Max Error | The overall error rate across all prepared bills must remain under the 1% cap. | N/A | No | N/A | Reported data not available.
2021-22 | Billing Complaints | Billing Disputes (No inspection) | Correcting billing errors where no additional on-site inspection or information is required. | When a billing complaint is raised and no on-site investigation is needed, the revised bill must be issued within 24 working hours. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2021-22 | Billing Complaints | Billing Disputes (LT - Inspection) | Correcting billing errors where inspection or meter verification is needed for Low Tension (LT) consumers. | If a billing complaint requires field inspection or meter checking for LT consumers, the licensee must issue the revised bill within 7 working days. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2021-22 | Billing Complaints | Billing Disputes (HT - Inspection) | Correcting billing errors where inspection or meter verification is needed for High Tension (HT) consumers. | For HT consumer billing disputes requiring on-site verification, the revised bill must be completed and issued within 15 days. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2021-22 | Metering Complaints | System Meter Health | The maximum allowable proportion of active meters that are malfunctioning or defective. | The utility must manage its network such that the overall proportion of faulty meters in service does not exceed 3% of the total meters. | 3% Max Defect | The overall percentage of faulty meters in service must be kept below the 3% ceiling. | N/A | No | N/A | Reported data not available.
2021-22 | Metering Complaints | Defective Meter Resolution (Urban) | Testing and replacing defective, creeping, or stuck meters in urban areas. | For defective meters in urban areas, the licensee must inspect them within 7 days and complete the replacement within 15 days thereafter. | 99 | At least 99% of cases in urban areas must be resolved within the specified timelines. | N/A | No | N/A | Reported data not available.
2021-22 | Metering Complaints | Defective Meter Resolution (Rural) | Testing and replacing defective, creeping, or stuck meters in rural areas. | The utility must inspect a reported defective meter in rural areas within 15 days and replace it within 15 days of that inspection. | 98 | At least 98% of cases in rural areas must be resolved within the specified timelines. | N/A | No | N/A | Reported data not available.
2021-22 | Metering Complaints | Burnt Meter (Licensee Cause) | Replacing burnt meters due to network failures (such as high voltage or loose contacts). | When a meter burns out due to utility-attributable factors, it must be replaced at licensee cost within 7 days. | 99% (U) / 98% (R) | At least 99% of urban and 98% of rural complaints must be resolved within the standard. | N/A | No | N/A | Reported data not available.
2021-22 | Metering Complaints | Burnt Meter (Consumer Cause) | Replacing burnt meters due to consumer overloading, tampering, or water exposure. | If a meter is burnt due to consumer-side issues, the licensee must replace it within 14 days of receiving payment or a replacement meter. | 99% (U) / 98% (R) | At least 99% of urban and 98% of rural complaints must be resolved within the standard. | N/A | No | N/A | Reported data not available.
2021-22 | Voltage Issues | Voltage Unbalance | Limit on the symmetry deviation among phase voltages at the point of supply. | The phase voltage unbalance at the consumer's point of supply must be maintained so that it does not exceed 3%. | 98 | At least 98% of cases related to voltage unbalance must be resolved. | N/A | No | N/A | Reported data not available.
2021-22 | Voltage Issues | Voltage Fluctuations (No network expansion) | Resolving voltage issues where system network expansion is not required. | The licensee must resolve complaints regarding voltage levels within 10 days when no network expansion is required. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2021-22 | Voltage Issues | Voltage Fluctuations (System Upgrade) | Resolving voltage issues where system capacity reinforcement or upgrade is required. | Where resolving voltage fluctuations requires system up-gradation or network enhancement, the works must be completed within 120 days. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2021-22 | Voltage Issues | Voltage Fluctuations (Substation Erection) | Resolving voltage issues when a new substation needs to be erected. | When resolving a voltage issue requires erecting a new substation, the utility must complete it within the time period approved by the Commission. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2021-22 | New Connections / Load Changes | Feasible Connection (Existing network) | Releasing supply where distribution mains are already in place. | The distribution licensee must release a new electricity connection within 30 days of receiving a completed application and requisite charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2021-22 | New Connections / Load Changes | Low Tension (LT) Network Expansion | Releasing LT supply when distribution main extension is required. | Where an LT connection requires expanding or enhancing the distribution network, the supply must be released within 30 days of receiving payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2021-22 | New Connections / Load Changes | High Tension (HT) Connection - 11 KV | Releasing 11 KV supply when network extension is required. | The licensee must complete the necessary 11 KV network expansion and release supply within 60 days of payment of prescribed charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2021-22 | New Connections / Load Changes | High Tension (HT) Connection - 33 KV | Releasing 33 KV supply when network extension is required. | For new HT 33 KV connections requiring network extension, the licensee must complete the work and release supply within 90 days of payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2021-22 | New Connections / Load Changes | Extra High Tension (EHT) Connection | Releasing EHT supply when network extension is required. | When releasing an Extra High Tension supply involves network extension, the connection must be completed and energized within 180 days of payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2021-22 | New Connections / Load Changes | Substation Erection | Releasing supply when a new substation must be erected. | If releasing a new connection requires erecting a substation, the licensee must complete the installation within the timeframe approved by the Commission. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2021-22 | Consumer Service Alterations | Title Transfer | Processing the transfer of ownership of a service connection to a new owner. | The licensee must process and finalize the transfer of connection ownership within 7 days of receiving the documents and prescribed fee. | 98 | At least 98% of cases related to title transfer must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
2021-22 | Consumer Service Alterations | Category Conversion | Processing the change of consumer/tariff category. | A request for tariff or category conversion must be processed and completed by the licensee within 7 days of receiving the required documents. | 98 | At least 98% of cases related to conversion must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
2021-22 | Consumer Service Alterations | Load Reduction | Processing a consumer's request to reduce contract demand. | The licensee must complete the load reduction process within the notice period specified in the Electricity Supply Code. | 98 | At least 98% of load reduction requests must be completed within the notice period. | N/A | No | N/A | Reported data not available.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Restoration of Power Supply | Normal Fuse-off Calls (Urban) | Replacing blown Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | The distribution licensee must replace blown fuses and restore power supply within 4 hours in cities and towns. | 95 | At least 95% of calls received must be rectified within the specified time limit. | N/A | No | N/A | Reported data not available.
2022-23 | Restoration of Power Supply | Normal Fuse-off Calls (Rural) | Replacing blown Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | In rural areas, the licensee is mandated to replace blown fuses and restore the supply within 24 hours. | 95 | At least 95% of calls received must be rectified within the specified time limit. | N/A | No | N/A | Reported data not available.
2022-23 | Restoration of Power Supply | Overhead Line / Cable Breakdowns (Urban) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | For overhead line or cable failures in cities and towns, the utility must resolve the breakdown and restore electricity within 6 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2022-23 | Restoration of Power Supply | Overhead Line / Cable Breakdowns (Rural) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | Power supply restoration following an overhead line or cable breakdown in rural areas must be completed within 36 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2022-23 | Restoration of Power Supply | Underground Cable Breakdowns (Urban) | Locating, repairing, and re-energising the system following faults in underground cables. | The licensee is required to locate, repair, and re-energize the network within 24 hours of an underground cable fault in urban areas. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2022-23 | Restoration of Power Supply | Underground Cable Breakdowns (Rural) | Locating, repairing, and re-energising the system following faults in underground cables. | Underground cable faults in rural areas must be located and fully repaired to restore supply within 48 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2022-23 | Restoration of Power Supply | Distribution Transformer Failure (Urban) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | The utility must replace or repair a failed distribution transformer and restore supply to consumers within 24 hours in urban areas. | 95 | At least 95% of failed transformers must be replaced within the specified time limit. | N/A | No | N/A | Reported data not available.
2022-23 | Restoration of Power Supply | Distribution Transformer Failure (Rural) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | Following a distribution transformer failure in rural areas, the company must complete replacement and restore supply within 72 hours. | 95 | At least 95% of failed transformers must be replaced within the specified time limit. | N/A | No | N/A | Reported data not available.
2022-23 | System Outages | Scheduled Outages (Duration) | Pre-arranged shut-downs of equipment and lines for necessary maintenance work. | The maximum duration of a pre-planned maintenance outage is strictly capped at 12 hours in a single stretch. | 95 | At least 95% of scheduled outages must comply with the maximum duration standard. | N/A | No | N/A | Reported data not available.
2022-23 | System Outages | Scheduled Outages (Restoration) | Pre-arranged shut-downs of equipment and lines for necessary maintenance work. | During pre-arranged maintenance, the utility must ensure power supply is fully restored not later than 6:00 PM. | 95 | At least 95% of planned outages must have supply restored by 6:00 PM. | N/A | No | N/A | Reported data not available.
2022-23 | Street Light Complaints | Street Light Faults | Rectification of line faults and replacement of public street lighting fixtures. | The licensee must rectify line faults or replace fused and defective public street lighting fixtures as soon as possible. | 90 | At least 90% of street light complaints must be resolved. | N/A | No | N/A | Reported data not available.
2022-23 | Billing Complaints | Billing Accuracy | Total allowable rate of billing errors across all prepared accounts. | The total number of billing mistakes across all processed accounts must be kept under a maximum limit of 1% of total bills prepared. | 1% Max Error | The overall error rate across all prepared bills must remain under the 1% cap. | N/A | No | N/A | Reported data not available.
2022-23 | Billing Complaints | Billing Disputes (No inspection) | Correcting billing errors where no additional on-site inspection or information is required. | When a billing complaint is raised and no on-site investigation is needed, the revised bill must be issued within 24 working hours. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2022-23 | Billing Complaints | Billing Disputes (LT - Inspection) | Correcting billing errors where inspection or meter verification is needed for Low Tension (LT) consumers. | If a billing complaint requires field inspection or meter checking for LT consumers, the licensee must issue the revised bill within 7 working days. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2022-23 | Billing Complaints | Billing Disputes (HT - Inspection) | Correcting billing errors where inspection or meter verification is needed for High Tension (HT) consumers. | For HT consumer billing disputes requiring on-site verification, the revised bill must be completed and issued within 15 days. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2022-23 | Metering Complaints | System Meter Health | The maximum allowable proportion of active meters that are malfunctioning or defective. | The utility must manage its network such that the overall proportion of faulty meters in service does not exceed 3% of the total meters. | 3% Max Defect | The overall percentage of faulty meters in service must be kept below the 3% ceiling. | N/A | No | N/A | Reported data not available.
2022-23 | Metering Complaints | Defective Meter Resolution (Urban) | Testing and replacing defective, creeping, or stuck meters in urban areas. | For defective meters in urban areas, the licensee must inspect them within 7 days and complete the replacement within 15 days thereafter. | 99 | At least 99% of cases in urban areas must be resolved within the specified timelines. | N/A | No | N/A | Reported data not available.
2022-23 | Metering Complaints | Defective Meter Resolution (Rural) | Testing and replacing defective, creeping, or stuck meters in rural areas. | The utility must inspect a reported defective meter in rural areas within 15 days and replace it within 15 days of that inspection. | 98 | At least 98% of cases in rural areas must be resolved within the specified timelines. | N/A | No | N/A | Reported data not available.
2022-23 | Metering Complaints | Burnt Meter (Licensee Cause) | Replacing burnt meters due to network failures (such as high voltage or loose contacts). | When a meter burns out due to utility-attributable factors, it must be replaced at licensee cost within 7 days. | 99% (U) / 98% (R) | At least 99% of urban and 98% of rural complaints must be resolved within the standard. | N/A | No | N/A | Reported data not available.
2022-23 | Metering Complaints | Burnt Meter (Consumer Cause) | Replacing burnt meters due to consumer overloading, tampering, or water exposure. | If a meter is burnt due to consumer-side issues, the licensee must replace it within 14 days of receiving payment or a replacement meter. | 99% (U) / 98% (R) | At least 99% of urban and 98% of rural complaints must be resolved within the standard. | N/A | No | N/A | Reported data not available.
2022-23 | Voltage Issues | Voltage Unbalance | Limit on the symmetry deviation among phase voltages at the point of supply. | The phase voltage unbalance at the consumer's point of supply must be maintained so that it does not exceed 3%. | 98 | At least 98% of cases related to voltage unbalance must be resolved. | N/A | No | N/A | Reported data not available.
2022-23 | Voltage Issues | Voltage Fluctuations (No network expansion) | Resolving voltage issues where system network expansion is not required. | The licensee must resolve complaints regarding voltage levels within 10 days when no network expansion is required. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2022-23 | Voltage Issues | Voltage Fluctuations (System Upgrade) | Resolving voltage issues where system capacity reinforcement or upgrade is required. | Where resolving voltage fluctuations requires system up-gradation or network enhancement, the works must be completed within 120 days. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2022-23 | Voltage Issues | Voltage Fluctuations (Substation Erection) | Resolving voltage issues when a new substation needs to be erected. | When resolving a voltage issue requires erecting a new substation, the utility must complete it within the time period approved by the Commission. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2022-23 | New Connections / Load Changes | Feasible Connection (Existing network) | Releasing supply where distribution mains are already in place. | The distribution licensee must release a new electricity connection within 30 days of receiving a completed application and requisite charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2022-23 | New Connections / Load Changes | Low Tension (LT) Network Expansion | Releasing LT supply when distribution main extension is required. | Where an LT connection requires expanding or enhancing the distribution network, the supply must be released within 30 days of receiving payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2022-23 | New Connections / Load Changes | High Tension (HT) Connection - 11 KV | Releasing 11 KV supply when network extension is required. | The licensee must complete the necessary 11 KV network expansion and release supply within 60 days of payment of prescribed charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2022-23 | New Connections / Load Changes | High Tension (HT) Connection - 33 KV | Releasing 33 KV supply when network extension is required. | For new HT 33 KV connections requiring network extension, the licensee must complete the work and release supply within 90 days of payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2022-23 | New Connections / Load Changes | Extra High Tension (EHT) Connection | Releasing EHT supply when network extension is required. | When releasing an Extra High Tension supply involves network extension, the connection must be completed and energized within 180 days of payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2022-23 | New Connections / Load Changes | Substation Erection | Releasing supply when a new substation must be erected. | If releasing a new connection requires erecting a substation, the licensee must complete the installation within the timeframe approved by the Commission. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2022-23 | Consumer Service Alterations | Title Transfer | Processing the transfer of ownership of a service connection to a new owner. | The licensee must process and finalize the transfer of connection ownership within 7 days of receiving the documents and prescribed fee. | 98 | At least 98% of cases related to title transfer must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
2022-23 | Consumer Service Alterations | Category Conversion | Processing the change of consumer/tariff category. | A request for tariff or category conversion must be processed and completed by the licensee within 7 days of receiving the required documents. | 98 | At least 98% of cases related to conversion must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
2022-23 | Consumer Service Alterations | Load Reduction | Processing a consumer's request to reduce contract demand. | The licensee must complete the load reduction process within the notice period specified in the Electricity Supply Code. | 98 | At least 98% of load reduction requests must be completed within the notice period. | N/A | No | N/A | Reported data not available.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Restoration of Power Supply | Normal Fuse-off Calls (Urban) | Replacing blown Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | The distribution licensee must replace blown fuses and restore power supply within 4 hours in cities and towns. | 95 | At least 95% of calls received must be rectified within the specified time limit. | N/A | No | N/A | Reported data not available.
2023-24 | Restoration of Power Supply | Normal Fuse-off Calls (Rural) | Replacing blown Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | In rural areas, the licensee is mandated to replace blown fuses and restore the supply within 24 hours. | 95 | At least 95% of calls received must be rectified within the specified time limit. | N/A | No | N/A | Reported data not available.
2023-24 | Restoration of Power Supply | Overhead Line / Cable Breakdowns (Urban) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | For overhead line or cable failures in cities and towns, the utility must resolve the breakdown and restore electricity within 6 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2023-24 | Restoration of Power Supply | Overhead Line / Cable Breakdowns (Rural) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | Power supply restoration following an overhead line or cable breakdown in rural areas must be completed within 36 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2023-24 | Restoration of Power Supply | Underground Cable Breakdowns (Urban) | Locating, repairing, and re-energising the system following faults in underground cables. | The licensee is required to locate, repair, and re-energize the network within 24 hours of an underground cable fault in urban areas. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2023-24 | Restoration of Power Supply | Underground Cable Breakdowns (Rural) | Locating, repairing, and re-energising the system following faults in underground cables. | Underground cable faults in rural areas must be located and fully repaired to restore supply within 48 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2023-24 | Restoration of Power Supply | Distribution Transformer Failure (Urban) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | The utility must replace or repair a failed distribution transformer and restore supply to consumers within 24 hours in urban areas. | 95 | At least 95% of failed transformers must be replaced within the specified time limit. | N/A | No | N/A | Reported data not available.
2023-24 | Restoration of Power Supply | Distribution Transformer Failure (Rural) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | Following a distribution transformer failure in rural areas, the company must complete replacement and restore supply within 72 hours. | 95 | At least 95% of failed transformers must be replaced within the specified time limit. | N/A | No | N/A | Reported data not available.
2023-24 | System Outages | Scheduled Outages (Duration) | Pre-arranged shut-downs of equipment and lines for necessary maintenance work. | The maximum duration of a pre-planned maintenance outage is strictly capped at 12 hours in a single stretch. | 95 | At least 95% of scheduled outages must comply with the maximum duration standard. | N/A | No | N/A | Reported data not available.
2023-24 | System Outages | Scheduled Outages (Restoration) | Pre-arranged shut-downs of equipment and lines for necessary maintenance work. | During pre-arranged maintenance, the utility must ensure power supply is fully restored not later than 6:00 PM. | 95 | At least 95% of planned outages must have supply restored by 6:00 PM. | N/A | No | N/A | Reported data not available.
2023-24 | Street Light Complaints | Street Light Faults | Rectification of line faults and replacement of public street lighting fixtures. | The licensee must rectify line faults or replace fused and defective public street lighting fixtures as soon as possible. | 90 | At least 90% of street light complaints must be resolved. | N/A | No | N/A | Reported data not available.
2023-24 | Billing Complaints | Billing Accuracy | Total allowable rate of billing errors across all prepared accounts. | The total number of billing mistakes across all processed accounts must be kept under a maximum limit of 1% of total bills prepared. | 1% Max Error | The overall error rate across all prepared bills must remain under the 1% cap. | N/A | No | N/A | Reported data not available.
2023-24 | Billing Complaints | Billing Disputes (No inspection) | Correcting billing errors where no additional on-site inspection or information is required. | When a billing complaint is raised and no on-site investigation is needed, the revised bill must be issued within 24 working hours. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2023-24 | Billing Complaints | Billing Disputes (LT - Inspection) | Correcting billing errors where inspection or meter verification is needed for Low Tension (LT) consumers. | If a billing complaint requires field inspection or meter checking for LT consumers, the licensee must issue the revised bill within 7 working days. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2023-24 | Billing Complaints | Billing Disputes (HT - Inspection) | Correcting billing errors where inspection or meter verification is needed for High Tension (HT) consumers. | For HT consumer billing disputes requiring on-site verification, the revised bill must be completed and issued within 15 days. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2023-24 | Metering Complaints | System Meter Health | The maximum allowable proportion of active meters that are malfunctioning or defective. | The utility must manage its network such that the overall proportion of faulty meters in service does not exceed 3% of the total meters. | 3% Max Defect | The overall percentage of faulty meters in service must be kept below the 3% ceiling. | N/A | No | N/A | Reported data not available.
2023-24 | Metering Complaints | Defective Meter Resolution (Urban) | Testing and replacing defective, creeping, or stuck meters in urban areas. | For defective meters in urban areas, the licensee must inspect them within 7 days and complete the replacement within 15 days thereafter. | 99 | At least 99% of cases in urban areas must be resolved within the specified timelines. | N/A | No | N/A | Reported data not available.
2023-24 | Metering Complaints | Defective Meter Resolution (Rural) | Testing and replacing defective, creeping, or stuck meters in rural areas. | The utility must inspect a reported defective meter in rural areas within 15 days and replace it within 15 days of that inspection. | 98 | At least 98% of cases in rural areas must be resolved within the specified timelines. | N/A | No | N/A | Reported data not available.
2023-24 | Metering Complaints | Burnt Meter (Licensee Cause) | Replacing burnt meters due to network failures (such as high voltage or loose contacts). | When a meter burns out due to utility-attributable factors, it must be replaced at licensee cost within 7 days. | 99% (U) / 98% (R) | At least 99% of urban and 98% of rural complaints must be resolved within the standard. | N/A | No | N/A | Reported data not available.
2023-24 | Metering Complaints | Burnt Meter (Consumer Cause) | Replacing burnt meters due to consumer overloading, tampering, or water exposure. | If a meter is burnt due to consumer-side issues, the licensee must replace it within 14 days of receiving payment or a replacement meter. | 99% (U) / 98% (R) | At least 99% of urban and 98% of rural complaints must be resolved within the standard. | N/A | No | N/A | Reported data not available.
2023-24 | Voltage Issues | Voltage Unbalance | Limit on the symmetry deviation among phase voltages at the point of supply. | The phase voltage unbalance at the consumer's point of supply must be maintained so that it does not exceed 3%. | 98 | At least 98% of cases related to voltage unbalance must be resolved. | N/A | No | N/A | Reported data not available.
2023-24 | Voltage Issues | Voltage Fluctuations (No network expansion) | Resolving voltage issues where system network expansion is not required. | The licensee must resolve complaints regarding voltage levels within 10 days when no network expansion is required. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2023-24 | Voltage Issues | Voltage Fluctuations (System Upgrade) | Resolving voltage issues where system capacity reinforcement or upgrade is required. | Where resolving voltage fluctuations requires system up-gradation or network enhancement, the works must be completed within 120 days. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2023-24 | Voltage Issues | Voltage Fluctuations (Substation Erection) | Resolving voltage issues when a new substation needs to be erected. | When resolving a voltage issue requires erecting a new substation, the utility must complete it within the time period approved by the Commission. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2023-24 | New Connections / Load Changes | Feasible Connection (Existing network) | Releasing supply where distribution mains are already in place. | The distribution licensee must release a new electricity connection within 30 days of receiving a completed application and requisite charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2023-24 | New Connections / Load Changes | Low Tension (LT) Network Expansion | Releasing LT supply when distribution main extension is required. | Where an LT connection requires expanding or enhancing the distribution network, the supply must be released within 30 days of receiving payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2023-24 | New Connections / Load Changes | High Tension (HT) Connection - 11 KV | Releasing 11 KV supply when network extension is required. | The licensee must complete the necessary 11 KV network expansion and release supply within 60 days of payment of prescribed charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2023-24 | New Connections / Load Changes | High Tension (HT) Connection - 33 KV | Releasing 33 KV supply when network extension is required. | For new HT 33 KV connections requiring network extension, the licensee must complete the work and release supply within 90 days of payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2023-24 | New Connections / Load Changes | Extra High Tension (EHT) Connection | Releasing EHT supply when network extension is required. | When releasing an Extra High Tension supply involves network extension, the connection must be completed and energized within 180 days of payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2023-24 | New Connections / Load Changes | Substation Erection | Releasing supply when a new substation must be erected. | If releasing a new connection requires erecting a substation, the licensee must complete the installation within the timeframe approved by the Commission. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2023-24 | Consumer Service Alterations | Title Transfer | Processing the transfer of ownership of a service connection to a new owner. | The licensee must process and finalize the transfer of connection ownership within 7 days of receiving the documents and prescribed fee. | 98 | At least 98% of cases related to title transfer must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
2023-24 | Consumer Service Alterations | Category Conversion | Processing the change of consumer/tariff category. | A request for tariff or category conversion must be processed and completed by the licensee within 7 days of receiving the required documents. | 98 | At least 98% of cases related to conversion must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
2023-24 | Consumer Service Alterations | Load Reduction | Processing a consumer's request to reduce contract demand. | The licensee must complete the load reduction process within the notice period specified in the Electricity Supply Code. | 98 | At least 98% of load reduction requests must be completed within the notice period. | N/A | No | N/A | Reported data not available.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Restoration of Power Supply | Normal Fuse-off Calls (Urban) | Replacing blown Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | The distribution licensee must replace blown fuses and restore power supply within 4 hours in cities and towns. | 95 | At least 95% of calls received must be rectified within the specified time limit. | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Normal Fuse-off Calls (Rural) | Replacing blown Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | In rural areas, the licensee is mandated to replace blown fuses and restore the supply within 24 hours. | 95 | At least 95% of calls received must be rectified within the specified time limit. | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Overhead Line / Cable Breakdowns (Urban) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | For overhead line or cable failures in cities and towns, the utility must resolve the breakdown and restore electricity within 6 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Overhead Line / Cable Breakdowns (Rural) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | Power supply restoration following an overhead line or cable breakdown in rural areas must be completed within 36 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Underground Cable Breakdowns (Urban) | Locating, repairing, and re-energising the system following faults in underground cables. | The licensee is required to locate, repair, and re-energize the network within 24 hours of an underground cable fault in urban areas. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Underground Cable Breakdowns (Rural) | Locating, repairing, and re-energising the system following faults in underground cables. | Underground cable faults in rural areas must be located and fully repaired to restore supply within 48 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Distribution Transformer Failure (Urban) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | The utility must replace or repair a failed distribution transformer and restore supply to consumers within 24 hours in urban areas. | 95 | At least 95% of failed transformers must be replaced within the specified time limit. | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Distribution Transformer Failure (Rural) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | Following a distribution transformer failure in rural areas, the company must complete replacement and restore supply within 72 hours. | 95 | At least 95% of failed transformers must be replaced within the specified time limit. | N/A | No | N/A | Reported data not available.
2024-25 | System Outages | Scheduled Outages (Duration) | Pre-arranged shut-downs of equipment and lines for necessary maintenance work. | The maximum duration of a pre-planned maintenance outage is strictly capped at 12 hours in a single stretch. | 95 | At least 95% of scheduled outages must comply with the maximum duration standard. | N/A | No | N/A | Reported data not available.
2024-25 | System Outages | Scheduled Outages (Restoration) | Pre-arranged shut-downs of equipment and lines for necessary maintenance work. | During pre-arranged maintenance, the utility must ensure power supply is fully restored not later than 6:00 PM. | 95 | At least 95% of planned outages must have supply restored by 6:00 PM. | N/A | No | N/A | Reported data not available.
2024-25 | Street Light Complaints | Street Light Faults | Rectification of line faults and replacement of public street lighting fixtures. | The licensee must rectify line faults or replace fused and defective public street lighting fixtures as soon as possible. | 90 | At least 90% of street light complaints must be resolved. | N/A | No | N/A | Reported data not available.
2024-25 | Billing Complaints | Billing Accuracy | Total allowable rate of billing errors across all prepared accounts. | The total number of billing mistakes across all processed accounts must be kept under a maximum limit of 1% of total bills prepared. | 1% Max Error | The overall error rate across all prepared bills must remain under the 1% cap. | N/A | No | N/A | Reported data not available.
2024-25 | Billing Complaints | Billing Disputes (No inspection) | Correcting billing errors where no additional on-site inspection or information is required. | When a billing complaint is raised and no on-site investigation is needed, the revised bill must be issued within 24 working hours. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2024-25 | Billing Complaints | Billing Disputes (LT - Inspection) | Correcting billing errors where inspection or meter verification is needed for Low Tension (LT) consumers. | If a billing complaint requires field inspection or meter checking for LT consumers, the licensee must issue the revised bill within 7 working days. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2024-25 | Billing Complaints | Billing Disputes (HT - Inspection) | Correcting billing errors where inspection or meter verification is needed for High Tension (HT) consumers. | For HT consumer billing disputes requiring on-site verification, the revised bill must be completed and issued within 15 days. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2024-25 | Metering Complaints | System Meter Health | The maximum allowable proportion of active meters that are malfunctioning or defective. | The utility must manage its network such that the overall proportion of faulty meters in service does not exceed 3% of the total meters. | 3% Max Defect | The overall percentage of faulty meters in service must be kept below the 3% ceiling. | N/A | No | N/A | Reported data not available.
2024-25 | Metering Complaints | Defective Meter Resolution (Urban) | Testing and replacing defective, creeping, or stuck meters in urban areas. | For defective meters in urban areas, the licensee must inspect them within 7 days and complete the replacement within 15 days thereafter. | 99 | At least 99% of cases in urban areas must be resolved within the specified timelines. | N/A | No | N/A | Reported data not available.
2024-25 | Metering Complaints | Defective Meter Resolution (Rural) | Testing and replacing defective, creeping, or stuck meters in rural areas. | The utility must inspect a reported defective meter in rural areas within 15 days and replace it within 15 days of that inspection. | 98 | At least 98% of cases in rural areas must be resolved within the specified timelines. | N/A | No | N/A | Reported data not available.
2024-25 | Metering Complaints | Burnt Meter (Licensee Cause) | Replacing burnt meters due to network failures (such as high voltage or loose contacts). | When a meter burns out due to utility-attributable factors, it must be replaced at licensee cost within 7 days. | 99% (U) / 98% (R) | At least 99% of urban and 98% of rural complaints must be resolved within the standard. | N/A | No | N/A | Reported data not available.
2024-25 | Metering Complaints | Burnt Meter (Consumer Cause) | Replacing burnt meters due to consumer overloading, tampering, or water exposure. | If a meter is burnt due to consumer-side issues, the licensee must replace it within 14 days of receiving payment or a replacement meter. | 99% (U) / 98% (R) | At least 99% of urban and 98% of rural complaints must be resolved within the standard. | N/A | No | N/A | Reported data not available.
2024-25 | Voltage Issues | Voltage Unbalance | Limit on the symmetry deviation among phase voltages at the point of supply. | The phase voltage unbalance at the consumer's point of supply must be maintained so that it does not exceed 3%. | 98 | At least 98% of cases related to voltage unbalance must be resolved. | N/A | No | N/A | Reported data not available.
2024-25 | Voltage Issues | Voltage Fluctuations (No network expansion) | Resolving voltage issues where system network expansion is not required. | The licensee must resolve complaints regarding voltage levels within 10 days when no network expansion is required. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2024-25 | Voltage Issues | Voltage Fluctuations (System Upgrade) | Resolving voltage issues where system capacity reinforcement or upgrade is required. | Where resolving voltage fluctuations requires system up-gradation or network enhancement, the works must be completed within 120 days. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2024-25 | Voltage Issues | Voltage Fluctuations (Substation Erection) | Resolving voltage issues when a new substation needs to be erected. | When resolving a voltage issue requires erecting a new substation, the utility must complete it within the time period approved by the Commission. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2024-25 | New Connections / Load Changes | Feasible Connection (Existing network) | Releasing supply where distribution mains are already in place. | The distribution licensee must release a new electricity connection within 30 days of receiving a completed application and requisite charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2024-25 | New Connections / Load Changes | Low Tension (LT) Network Expansion | Releasing LT supply when distribution main extension is required. | Where an LT connection requires expanding or enhancing the distribution network, the supply must be released within 30 days of receiving payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2024-25 | New Connections / Load Changes | High Tension (HT) Connection - 11 KV | Releasing 11 KV supply when network extension is required. | The licensee must complete the necessary 11 KV network expansion and release supply within 60 days of payment of prescribed charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2024-25 | New Connections / Load Changes | High Tension (HT) Connection - 33 KV | Releasing 33 KV supply when network extension is required. | For new HT 33 KV connections requiring network extension, the licensee must complete the work and release supply within 90 days of payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2024-25 | New Connections / Load Changes | Extra High Tension (EHT) Connection | Releasing EHT supply when network extension is required. | When releasing an Extra High Tension supply involves network extension, the connection must be completed and energized within 180 days of payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2024-25 | New Connections / Load Changes | Substation Erection | Releasing supply when a new substation must be erected. | If releasing a new connection requires erecting a substation, the licensee must complete the installation within the timeframe approved by the Commission. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2024-25 | Consumer Service Alterations | Title Transfer | Processing the transfer of ownership of a service connection to a new owner. | The licensee must process and finalize the transfer of connection ownership within 7 days of receiving the documents and prescribed fee. | 98 | At least 98% of cases related to title transfer must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
2024-25 | Consumer Service Alterations | Category Conversion | Processing the change of consumer/tariff category. | A request for tariff or category conversion must be processed and completed by the licensee within 7 days of receiving the required documents. | 98 | At least 98% of cases related to conversion must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
2024-25 | Consumer Service Alterations | Load Reduction | Processing a consumer's request to reduce contract demand. | The licensee must complete the load reduction process within the notice period specified in the Electricity Supply Code. | 98 | At least 98% of load reduction requests must be completed within the notice period. | N/A | No | N/A | Reported data not available.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Restoration of Power Supply | Normal Fuse-off Calls (Urban) | Replacing blown Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | The distribution licensee must replace blown fuses and restore power supply within 4 hours in cities and towns. | 95 | At least 95% of calls received must be rectified within the specified time limit. | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Normal Fuse-off Calls (Rural) | Replacing blown Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | In rural areas, the licensee is mandated to replace blown fuses and restore the supply within 24 hours. | 95 | At least 95% of calls received must be rectified within the specified time limit. | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Overhead Line / Cable Breakdowns (Urban) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | For overhead line or cable failures in cities and towns, the utility must resolve the breakdown and restore electricity within 6 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Overhead Line / Cable Breakdowns (Rural) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | Power supply restoration following an overhead line or cable breakdown in rural areas must be completed within 36 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Underground Cable Breakdowns (Urban) | Locating, repairing, and re-energising the system following faults in underground cables. | The licensee is required to locate, repair, and re-energize the network within 24 hours of an underground cable fault in urban areas. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Underground Cable Breakdowns (Rural) | Locating, repairing, and re-energising the system following faults in underground cables. | Underground cable faults in rural areas must be located and fully repaired to restore supply within 48 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Distribution Transformer Failure (Urban) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | The utility must replace or repair a failed distribution transformer and restore supply to consumers within 24 hours in urban areas. | 95 | At least 95% of failed transformers must be replaced within the specified time limit. | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Distribution Transformer Failure (Rural) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | Following a distribution transformer failure in rural areas, the company must complete replacement and restore supply within 72 hours. | 95 | At least 95% of failed transformers must be replaced within the specified time limit. | N/A | No | N/A | Reported data not available.
2025-26 | System Outages | Scheduled Outages (Duration) | Pre-arranged shut-downs of equipment and lines for necessary maintenance work. | The maximum duration of a pre-planned maintenance outage is strictly capped at 12 hours in a single stretch. | 95 | At least 95% of scheduled outages must comply with the maximum duration standard. | N/A | No | N/A | Reported data not available.
2025-26 | System Outages | Scheduled Outages (Restoration) | Pre-arranged shut-downs of equipment and lines for necessary maintenance work. | During pre-arranged maintenance, the utility must ensure power supply is fully restored not later than 6:00 PM. | 95 | At least 95% of planned outages must have supply restored by 6:00 PM. | N/A | No | N/A | Reported data not available.
2025-26 | Street Light Complaints | Street Light Faults | Rectification of line faults and replacement of public street lighting fixtures. | The licensee must rectify line faults or replace fused and defective public street lighting fixtures as soon as possible. | 90 | At least 90% of street light complaints must be resolved. | N/A | No | N/A | Reported data not available.
2025-26 | Billing Complaints | Billing Accuracy | Total allowable rate of billing errors across all prepared accounts. | The total number of billing mistakes across all processed accounts must be kept under a maximum limit of 1% of total bills prepared. | 1% Max Error | The overall error rate across all prepared bills must remain under the 1% cap. | N/A | No | N/A | Reported data not available.
2025-26 | Billing Complaints | Billing Disputes (No inspection) | Correcting billing errors where no additional on-site inspection or information is required. | When a billing complaint is raised and no on-site investigation is needed, the revised bill must be issued within 24 working hours. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2025-26 | Billing Complaints | Billing Disputes (LT - Inspection) | Correcting billing errors where inspection or meter verification is needed for Low Tension (LT) consumers. | If a billing complaint requires field inspection or meter checking for LT consumers, the licensee must issue the revised bill within 7 working days. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2025-26 | Billing Complaints | Billing Disputes (HT - Inspection) | Correcting billing errors where inspection or meter verification is needed for High Tension (HT) consumers. | For HT consumer billing disputes requiring on-site verification, the revised bill must be completed and issued within 15 days. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2025-26 | Metering Complaints | System Meter Health | The maximum allowable proportion of active meters that are malfunctioning or defective. | The utility must manage its network such that the overall proportion of faulty meters in service does not exceed 3% of the total meters. | 3% Max Defect | The overall percentage of faulty meters in service must be kept below the 3% ceiling. | N/A | No | N/A | Reported data not available.
2025-26 | Metering Complaints | Defective Meter Resolution (Urban) | Testing and replacing defective, creeping, or stuck meters in urban areas. | For defective meters in urban areas, the licensee must inspect them within 7 days and complete the replacement within 15 days thereafter. | 99 | At least 99% of cases in urban areas must be resolved within the specified timelines. | N/A | No | N/A | Reported data not available.
2025-26 | Metering Complaints | Defective Meter Resolution (Rural) | Testing and replacing defective, creeping, or stuck meters in rural areas. | The utility must inspect a reported defective meter in rural areas within 15 days and replace it within 15 days of that inspection. | 98 | At least 98% of cases in rural areas must be resolved within the specified timelines. | N/A | No | N/A | Reported data not available.
2025-26 | Metering Complaints | Burnt Meter (Licensee Cause) | Replacing burnt meters due to network failures (such as high voltage or loose contacts). | When a meter burns out due to utility-attributable factors, it must be replaced at licensee cost within 7 days. | 99% (U) / 98% (R) | At least 99% of urban and 98% of rural complaints must be resolved within the standard. | N/A | No | N/A | Reported data not available.
2025-26 | Metering Complaints | Burnt Meter (Consumer Cause) | Replacing burnt meters due to consumer overloading, tampering, or water exposure. | If a meter is burnt due to consumer-side issues, the licensee must replace it within 14 days of receiving payment or a replacement meter. | 99% (U) / 98% (R) | At least 99% of urban and 98% of rural complaints must be resolved within the standard. | N/A | No | N/A | Reported data not available.
2025-26 | Voltage Issues | Voltage Unbalance | Limit on the symmetry deviation among phase voltages at the point of supply. | The phase voltage unbalance at the consumer's point of supply must be maintained so that it does not exceed 3%. | 98 | At least 98% of cases related to voltage unbalance must be resolved. | N/A | No | N/A | Reported data not available.
2025-26 | Voltage Issues | Voltage Fluctuations (No network expansion) | Resolving voltage issues where system network expansion is not required. | The licensee must resolve complaints regarding voltage levels within 10 days when no network expansion is required. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2025-26 | Voltage Issues | Voltage Fluctuations (System Upgrade) | Resolving voltage issues where system capacity reinforcement or upgrade is required. | Where resolving voltage fluctuations requires system up-gradation or network enhancement, the works must be completed within 120 days. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2025-26 | Voltage Issues | Voltage Fluctuations (Substation Erection) | Resolving voltage issues when a new substation needs to be erected. | When resolving a voltage issue requires erecting a new substation, the utility must complete it within the time period approved by the Commission. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2025-26 | New Connections / Load Changes | Feasible Connection (Existing network) | Releasing supply where distribution mains are already in place. | The distribution licensee must release a new electricity connection within 30 days of receiving a completed application and requisite charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2025-26 | New Connections / Load Changes | Low Tension (LT) Network Expansion | Releasing LT supply when distribution main extension is required. | Where an LT connection requires expanding or enhancing the distribution network, the supply must be released within 30 days of receiving payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2025-26 | New Connections / Load Changes | High Tension (HT) Connection - 11 KV | Releasing 11 KV supply when network extension is required. | The licensee must complete the necessary 11 KV network expansion and release supply within 60 days of payment of prescribed charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2025-26 | New Connections / Load Changes | High Tension (HT) Connection - 33 KV | Releasing 33 KV supply when network extension is required. | For new HT 33 KV connections requiring network extension, the licensee must complete the work and release supply within 90 days of payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2025-26 | New Connections / Load Changes | Extra High Tension (EHT) Connection | Releasing EHT supply when network extension is required. | When releasing an Extra High Tension supply involves network extension, the connection must be completed and energized within 180 days of payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2025-26 | New Connections / Load Changes | Substation Erection | Releasing supply when a new substation must be erected. | If releasing a new connection requires erecting a substation, the licensee must complete the installation within the timeframe approved by the Commission. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2025-26 | Consumer Service Alterations | Title Transfer | Processing the transfer of ownership of a service connection to a new owner. | The licensee must process and finalize the transfer of connection ownership within 7 days of receiving the documents and prescribed fee. | 98 | At least 98% of cases related to title transfer must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
2025-26 | Consumer Service Alterations | Category Conversion | Processing the change of consumer/tariff category. | A request for tariff or category conversion must be processed and completed by the licensee within 7 days of receiving the required documents. | 98 | At least 98% of cases related to conversion must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
2025-26 | Consumer Service Alterations | Load Reduction | Processing a consumer's request to reduce contract demand. | The licensee must complete the load reduction process within the notice period specified in the Electricity Supply Code. | 98 | At least 98% of load reduction requests must be completed within the notice period. | N/A | No | N/A | Reported data not available.

## SBPDCL, BIHAR
South Bihar Power Distribution Company Limited
Bihar Electricity Regulatory Commission (Standards of Performance of Distribution Licensee) Regulations, 2006 | Bihar Electricity Regulatory Commission (Standards of Performance of Distribution Licensee) (First Amendment) Regulations, 2012 | Bihar Electricity Regulatory Commission (Standards of Performance of Distribution Licensee) (First Amendment) Regulations, 2017
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Restoration of Power Supply | Normal Fuse-off Calls (Urban) | Replacing blown Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | The distribution licensee must replace blown fuses and restore power supply within 4 hours in cities and towns. | 95 | At least 95% of calls received must be rectified within the specified time limit. | N/A | No | N/A | Reported data not available.
2021-22 | Restoration of Power Supply | Normal Fuse-off Calls (Rural) | Replacing blown Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | In rural areas, the licensee is mandated to replace blown fuses and restore the supply within 24 hours. | 95 | At least 95% of calls received must be rectified within the specified time limit. | N/A | No | N/A | Reported data not available.
2021-22 | Restoration of Power Supply | Overhead Line / Cable Breakdowns (Urban) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | For overhead line or cable failures in cities and towns, the utility must resolve the breakdown and restore electricity within 6 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2021-22 | Restoration of Power Supply | Overhead Line / Cable Breakdowns (Rural) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | Power supply restoration following an overhead line or cable breakdown in rural areas must be completed within 36 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2021-22 | Restoration of Power Supply | Underground Cable Breakdowns (Urban) | Locating, repairing, and re-energising the system following faults in underground cables. | The licensee is required to locate, repair, and re-energize the network within 24 hours of an underground cable fault in urban areas. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2021-22 | Restoration of Power Supply | Underground Cable Breakdowns (Rural) | Locating, repairing, and re-energising the system following faults in underground cables. | Underground cable faults in rural areas must be located and fully repaired to restore supply within 48 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2021-22 | Restoration of Power Supply | Distribution Transformer Failure (Urban) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | The utility must replace or repair a failed distribution transformer and restore supply to consumers within 24 hours in urban areas. | 95 | At least 95% of failed transformers must be replaced within the specified time limit. | N/A | No | N/A | Reported data not available.
2021-22 | Restoration of Power Supply | Distribution Transformer Failure (Rural) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | Following a distribution transformer failure in rural areas, the company must complete replacement and restore supply within 72 hours. | 95 | At least 95% of failed transformers must be replaced within the specified time limit. | N/A | No | N/A | Reported data not available.
2021-22 | System Outages | Scheduled Outages (Duration) | Pre-arranged shut-downs of equipment and lines for necessary maintenance work. | The maximum duration of a pre-planned maintenance outage is strictly capped at 12 hours in a single stretch. | 95 | At least 95% of scheduled outages must comply with the maximum duration standard. | N/A | No | N/A | Reported data not available.
2021-22 | System Outages | Scheduled Outages (Restoration) | Pre-arranged shut-downs of equipment and lines for necessary maintenance work. | During pre-arranged maintenance, the utility must ensure power supply is fully restored not later than 6:00 PM. | 95 | At least 95% of planned outages must have supply restored by 6:00 PM. | N/A | No | N/A | Reported data not available.
2021-22 | Street Light Complaints | Street Light Faults | Rectification of line faults and replacement of public street lighting fixtures. | The licensee must rectify line faults or replace fused and defective public street lighting fixtures as soon as possible. | 90 | At least 90% of street light complaints must be resolved. | N/A | No | N/A | Reported data not available.
2021-22 | Billing Complaints | Billing Accuracy | Total allowable rate of billing errors across all prepared accounts. | The total number of billing mistakes across all processed accounts must be kept under a maximum limit of 1% of total bills prepared. | 1% Max Error | The overall error rate across all prepared bills must remain under the 1% cap. | N/A | No | N/A | Reported data not available.
2021-22 | Billing Complaints | Billing Disputes (No inspection) | Correcting billing errors where no additional on-site inspection or information is required. | When a billing complaint is raised and no on-site investigation is needed, the revised bill must be issued within 24 working hours. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2021-22 | Billing Complaints | Billing Disputes (LT - Inspection) | Correcting billing errors where inspection or meter verification is needed for Low Tension (LT) consumers. | If a billing complaint requires field inspection or meter checking for LT consumers, the licensee must issue the revised bill within 7 working days. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2021-22 | Billing Complaints | Billing Disputes (HT - Inspection) | Correcting billing errors where inspection or meter verification is needed for High Tension (HT) consumers. | For HT consumer billing disputes requiring on-site verification, the revised bill must be completed and issued within 15 days. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2021-22 | Metering Complaints | System Meter Health | The maximum allowable proportion of active meters that are malfunctioning or defective. | The utility must manage its network such that the overall proportion of faulty meters in service does not exceed 3% of the total meters. | 3% Max Defect | The overall percentage of faulty meters in service must be kept below the 3% ceiling. | N/A | No | N/A | Reported data not available.
2021-22 | Metering Complaints | Defective Meter Resolution (Urban) | Testing and replacing defective, creeping, or stuck meters in urban areas. | For defective meters in urban areas, the licensee must inspect them within 7 days and complete the replacement within 15 days thereafter. | 99 | At least 99% of cases in urban areas must be resolved within the specified timelines. | N/A | No | N/A | Reported data not available.
2021-22 | Metering Complaints | Defective Meter Resolution (Rural) | Testing and replacing defective, creeping, or stuck meters in rural areas. | The utility must inspect a reported defective meter in rural areas within 15 days and replace it within 15 days of that inspection. | 98 | At least 98% of cases in rural areas must be resolved within the specified timelines. | N/A | No | N/A | Reported data not available.
2021-22 | Metering Complaints | Burnt Meter (Licensee Cause) | Replacing burnt meters due to network failures (such as high voltage or loose contacts). | When a meter burns out due to utility-attributable factors, it must be replaced at licensee cost within 7 days. | 99% (U) / 98% (R) | At least 99% of urban and 98% of rural complaints must be resolved within the standard. | N/A | No | N/A | Reported data not available.
2021-22 | Metering Complaints | Burnt Meter (Consumer Cause) | Replacing burnt meters due to consumer overloading, tampering, or water exposure. | If a meter is burnt due to consumer-side issues, the licensee must replace it within 14 days of receiving payment or a replacement meter. | 99% (U) / 98% (R) | At least 99% of urban and 98% of rural complaints must be resolved within the standard. | N/A | No | N/A | Reported data not available.
2021-22 | Voltage Issues | Voltage Unbalance | Limit on the symmetry deviation among phase voltages at the point of supply. | The phase voltage unbalance at the consumer's point of supply must be maintained so that it does not exceed 3%. | 98 | At least 98% of cases related to voltage unbalance must be resolved. | N/A | No | N/A | Reported data not available.
2021-22 | Voltage Issues | Voltage Fluctuations (No network expansion) | Resolving voltage issues where system network expansion is not required. | The licensee must resolve complaints regarding voltage levels within 10 days when no network expansion is required. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2021-22 | Voltage Issues | Voltage Fluctuations (System Upgrade) | Resolving voltage issues where system capacity reinforcement or upgrade is required. | Where resolving voltage fluctuations requires system up-gradation or network enhancement, the works must be completed within 120 days. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2021-22 | Voltage Issues | Voltage Fluctuations (Substation Erection) | Resolving voltage issues when a new substation needs to be erected. | When resolving a voltage issue requires erecting a new substation, the utility must complete it within the time period approved by the Commission. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2021-22 | New Connections / Load Changes | Feasible Connection (Existing network) | Releasing supply where distribution mains are already in place. | The distribution licensee must release a new electricity connection within 30 days of receiving a completed application and requisite charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2021-22 | New Connections / Load Changes | Low Tension (LT) Network Expansion | Releasing LT supply when distribution main extension is required. | Where an LT connection requires expanding or enhancing the distribution network, the supply must be released within 30 days of receiving payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2021-22 | New Connections / Load Changes | High Tension (HT) Connection - 11 KV | Releasing 11 KV supply when network extension is required. | The licensee must complete the necessary 11 KV network expansion and release supply within 60 days of payment of prescribed charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2021-22 | New Connections / Load Changes | High Tension (HT) Connection - 33 KV | Releasing 33 KV supply when network extension is required. | For new HT 33 KV connections requiring network extension, the licensee must complete the work and release supply within 90 days of payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2021-22 | New Connections / Load Changes | Extra High Tension (EHT) Connection | Releasing EHT supply when network extension is required. | When releasing an Extra High Tension supply involves network extension, the connection must be completed and energized within 180 days of payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2021-22 | New Connections / Load Changes | Substation Erection | Releasing supply when a new substation must be erected. | If releasing a new connection requires erecting a substation, the licensee must complete the installation within the timeframe approved by the Commission. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2021-22 | Consumer Service Alterations | Title Transfer | Processing the transfer of ownership of a service connection to a new owner. | The licensee must process and finalize the transfer of connection ownership within 7 days of receiving the documents and prescribed fee. | 98 | At least 98% of cases related to title transfer must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
2021-22 | Consumer Service Alterations | Category Conversion | Processing the change of consumer/tariff category. | A request for tariff or category conversion must be processed and completed by the licensee within 7 days of receiving the required documents. | 98 | At least 98% of cases related to conversion must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
2021-22 | Consumer Service Alterations | Load Reduction | Processing a consumer's request to reduce contract demand. | The licensee must complete the load reduction process within the notice period specified in the Electricity Supply Code. | 98 | At least 98% of load reduction requests must be completed within the notice period. | N/A | No | N/A | Reported data not available.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Restoration of Power Supply | Normal Fuse-off Calls (Urban) | Replacing blown Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | The distribution licensee must replace blown fuses and restore power supply within 4 hours in cities and towns. | 95 | At least 95% of calls received must be rectified within the specified time limit. | N/A | No | N/A | Reported data not available.
2022-23 | Restoration of Power Supply | Normal Fuse-off Calls (Rural) | Replacing blown Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | In rural areas, the licensee is mandated to replace blown fuses and restore the supply within 24 hours. | 95 | At least 95% of calls received must be rectified within the specified time limit. | N/A | No | N/A | Reported data not available.
2022-23 | Restoration of Power Supply | Overhead Line / Cable Breakdowns (Urban) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | For overhead line or cable failures in cities and towns, the utility must resolve the breakdown and restore electricity within 6 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2022-23 | Restoration of Power Supply | Overhead Line / Cable Breakdowns (Rural) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | Power supply restoration following an overhead line or cable breakdown in rural areas must be completed within 36 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2022-23 | Restoration of Power Supply | Underground Cable Breakdowns (Urban) | Locating, repairing, and re-energising the system following faults in underground cables. | The licensee is required to locate, repair, and re-energize the network within 24 hours of an underground cable fault in urban areas. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2022-23 | Restoration of Power Supply | Underground Cable Breakdowns (Rural) | Locating, repairing, and re-energising the system following faults in underground cables. | Underground cable faults in rural areas must be located and fully repaired to restore supply within 48 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2022-23 | Restoration of Power Supply | Distribution Transformer Failure (Urban) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | The utility must replace or repair a failed distribution transformer and restore supply to consumers within 24 hours in urban areas. | 95 | At least 95% of failed transformers must be replaced within the specified time limit. | N/A | No | N/A | Reported data not available.
2022-23 | Restoration of Power Supply | Distribution Transformer Failure (Rural) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | Following a distribution transformer failure in rural areas, the company must complete replacement and restore supply within 72 hours. | 95 | At least 95% of failed transformers must be replaced within the specified time limit. | N/A | No | N/A | Reported data not available.
2022-23 | System Outages | Scheduled Outages (Duration) | Pre-arranged shut-downs of equipment and lines for necessary maintenance work. | The maximum duration of a pre-planned maintenance outage is strictly capped at 12 hours in a single stretch. | 95 | At least 95% of scheduled outages must comply with the maximum duration standard. | N/A | No | N/A | Reported data not available.
2022-23 | System Outages | Scheduled Outages (Restoration) | Pre-arranged shut-downs of equipment and lines for necessary maintenance work. | During pre-arranged maintenance, the utility must ensure power supply is fully restored not later than 6:00 PM. | 95 | At least 95% of planned outages must have supply restored by 6:00 PM. | N/A | No | N/A | Reported data not available.
2022-23 | Street Light Complaints | Street Light Faults | Rectification of line faults and replacement of public street lighting fixtures. | The licensee must rectify line faults or replace fused and defective public street lighting fixtures as soon as possible. | 90 | At least 90% of street light complaints must be resolved. | N/A | No | N/A | Reported data not available.
2022-23 | Billing Complaints | Billing Accuracy | Total allowable rate of billing errors across all prepared accounts. | The total number of billing mistakes across all processed accounts must be kept under a maximum limit of 1% of total bills prepared. | 1% Max Error | The overall error rate across all prepared bills must remain under the 1% cap. | N/A | No | N/A | Reported data not available.
2022-23 | Billing Complaints | Billing Disputes (No inspection) | Correcting billing errors where no additional on-site inspection or information is required. | When a billing complaint is raised and no on-site investigation is needed, the revised bill must be issued within 24 working hours. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2022-23 | Billing Complaints | Billing Disputes (LT - Inspection) | Correcting billing errors where inspection or meter verification is needed for Low Tension (LT) consumers. | If a billing complaint requires field inspection or meter checking for LT consumers, the licensee must issue the revised bill within 7 working days. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2022-23 | Billing Complaints | Billing Disputes (HT - Inspection) | Correcting billing errors where inspection or meter verification is needed for High Tension (HT) consumers. | For HT consumer billing disputes requiring on-site verification, the revised bill must be completed and issued within 15 days. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2022-23 | Metering Complaints | System Meter Health | The maximum allowable proportion of active meters that are malfunctioning or defective. | The utility must manage its network such that the overall proportion of faulty meters in service does not exceed 3% of the total meters. | 3% Max Defect | The overall percentage of faulty meters in service must be kept below the 3% ceiling. | N/A | No | N/A | Reported data not available.
2022-23 | Metering Complaints | Defective Meter Resolution (Urban) | Testing and replacing defective, creeping, or stuck meters in urban areas. | For defective meters in urban areas, the licensee must inspect them within 7 days and complete the replacement within 15 days thereafter. | 99 | At least 99% of cases in urban areas must be resolved within the specified timelines. | N/A | No | N/A | Reported data not available.
2022-23 | Metering Complaints | Defective Meter Resolution (Rural) | Testing and replacing defective, creeping, or stuck meters in rural areas. | The utility must inspect a reported defective meter in rural areas within 15 days and replace it within 15 days of that inspection. | 98 | At least 98% of cases in rural areas must be resolved within the specified timelines. | N/A | No | N/A | Reported data not available.
2022-23 | Metering Complaints | Burnt Meter (Licensee Cause) | Replacing burnt meters due to network failures (such as high voltage or loose contacts). | When a meter burns out due to utility-attributable factors, it must be replaced at licensee cost within 7 days. | 99% (U) / 98% (R) | At least 99% of urban and 98% of rural complaints must be resolved within the standard. | N/A | No | N/A | Reported data not available.
2022-23 | Metering Complaints | Burnt Meter (Consumer Cause) | Replacing burnt meters due to consumer overloading, tampering, or water exposure. | If a meter is burnt due to consumer-side issues, the licensee must replace it within 14 days of receiving payment or a replacement meter. | 99% (U) / 98% (R) | At least 99% of urban and 98% of rural complaints must be resolved within the standard. | N/A | No | N/A | Reported data not available.
2022-23 | Voltage Issues | Voltage Unbalance | Limit on the symmetry deviation among phase voltages at the point of supply. | The phase voltage unbalance at the consumer's point of supply must be maintained so that it does not exceed 3%. | 98 | At least 98% of cases related to voltage unbalance must be resolved. | N/A | No | N/A | Reported data not available.
2022-23 | Voltage Issues | Voltage Fluctuations (No network expansion) | Resolving voltage issues where system network expansion is not required. | The licensee must resolve complaints regarding voltage levels within 10 days when no network expansion is required. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2022-23 | Voltage Issues | Voltage Fluctuations (System Upgrade) | Resolving voltage issues where system capacity reinforcement or upgrade is required. | Where resolving voltage fluctuations requires system up-gradation or network enhancement, the works must be completed within 120 days. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2022-23 | Voltage Issues | Voltage Fluctuations (Substation Erection) | Resolving voltage issues when a new substation needs to be erected. | When resolving a voltage issue requires erecting a new substation, the utility must complete it within the time period approved by the Commission. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2022-23 | New Connections / Load Changes | Feasible Connection (Existing network) | Releasing supply where distribution mains are already in place. | The distribution licensee must release a new electricity connection within 30 days of receiving a completed application and requisite charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2022-23 | New Connections / Load Changes | Low Tension (LT) Network Expansion | Releasing LT supply when distribution main extension is required. | Where an LT connection requires expanding or enhancing the distribution network, the supply must be released within 30 days of receiving payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2022-23 | New Connections / Load Changes | High Tension (HT) Connection - 11 KV | Releasing 11 KV supply when network extension is required. | The licensee must complete the necessary 11 KV network expansion and release supply within 60 days of payment of prescribed charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2022-23 | New Connections / Load Changes | High Tension (HT) Connection - 33 KV | Releasing 33 KV supply when network extension is required. | For new HT 33 KV connections requiring network extension, the licensee must complete the work and release supply within 90 days of payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2022-23 | New Connections / Load Changes | Extra High Tension (EHT) Connection | Releasing EHT supply when network extension is required. | When releasing an Extra High Tension supply involves network extension, the connection must be completed and energized within 180 days of payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2022-23 | New Connections / Load Changes | Substation Erection | Releasing supply when a new substation must be erected. | If releasing a new connection requires erecting a substation, the licensee must complete the installation within the timeframe approved by the Commission. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2022-23 | Consumer Service Alterations | Title Transfer | Processing the transfer of ownership of a service connection to a new owner. | The licensee must process and finalize the transfer of connection ownership within 7 days of receiving the documents and prescribed fee. | 98 | At least 98% of cases related to title transfer must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
2022-23 | Consumer Service Alterations | Category Conversion | Processing the change of consumer/tariff category. | A request for tariff or category conversion must be processed and completed by the licensee within 7 days of receiving the required documents. | 98 | At least 98% of cases related to conversion must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
2022-23 | Consumer Service Alterations | Load Reduction | Processing a consumer's request to reduce contract demand. | The licensee must complete the load reduction process within the notice period specified in the Electricity Supply Code. | 98 | At least 98% of load reduction requests must be completed within the notice period. | N/A | No | N/A | Reported data not available.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Restoration of Power Supply | Normal Fuse-off Calls (Urban) | Replacing blown Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | The distribution licensee must replace blown fuses and restore power supply within 4 hours in cities and towns. | 95 | At least 95% of calls received must be rectified within the specified time limit. | N/A | No | N/A | Reported data not available.
2023-24 | Restoration of Power Supply | Normal Fuse-off Calls (Rural) | Replacing blown Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | In rural areas, the licensee is mandated to replace blown fuses and restore the supply within 24 hours. | 95 | At least 95% of calls received must be rectified within the specified time limit. | N/A | No | N/A | Reported data not available.
2023-24 | Restoration of Power Supply | Overhead Line / Cable Breakdowns (Urban) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | For overhead line or cable failures in cities and towns, the utility must resolve the breakdown and restore electricity within 6 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2023-24 | Restoration of Power Supply | Overhead Line / Cable Breakdowns (Rural) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | Power supply restoration following an overhead line or cable breakdown in rural areas must be completed within 36 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2023-24 | Restoration of Power Supply | Underground Cable Breakdowns (Urban) | Locating, repairing, and re-energising the system following faults in underground cables. | The licensee is required to locate, repair, and re-energize the network within 24 hours of an underground cable fault in urban areas. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2023-24 | Restoration of Power Supply | Underground Cable Breakdowns (Rural) | Locating, repairing, and re-energising the system following faults in underground cables. | Underground cable faults in rural areas must be located and fully repaired to restore supply within 48 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2023-24 | Restoration of Power Supply | Distribution Transformer Failure (Urban) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | The utility must replace or repair a failed distribution transformer and restore supply to consumers within 24 hours in urban areas. | 95 | At least 95% of failed transformers must be replaced within the specified time limit. | N/A | No | N/A | Reported data not available.
2023-24 | Restoration of Power Supply | Distribution Transformer Failure (Rural) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | Following a distribution transformer failure in rural areas, the company must complete replacement and restore supply within 72 hours. | 95 | At least 95% of failed transformers must be replaced within the specified time limit. | N/A | No | N/A | Reported data not available.
2023-24 | System Outages | Scheduled Outages (Duration) | Pre-arranged shut-downs of equipment and lines for necessary maintenance work. | The maximum duration of a pre-planned maintenance outage is strictly capped at 12 hours in a single stretch. | 95 | At least 95% of scheduled outages must comply with the maximum duration standard. | N/A | No | N/A | Reported data not available.
2023-24 | System Outages | Scheduled Outages (Restoration) | Pre-arranged shut-downs of equipment and lines for necessary maintenance work. | During pre-arranged maintenance, the utility must ensure power supply is fully restored not later than 6:00 PM. | 95 | At least 95% of planned outages must have supply restored by 6:00 PM. | N/A | No | N/A | Reported data not available.
2023-24 | Street Light Complaints | Street Light Faults | Rectification of line faults and replacement of public street lighting fixtures. | The licensee must rectify line faults or replace fused and defective public street lighting fixtures as soon as possible. | 90 | At least 90% of street light complaints must be resolved. | N/A | No | N/A | Reported data not available.
2023-24 | Billing Complaints | Billing Accuracy | Total allowable rate of billing errors across all prepared accounts. | The total number of billing mistakes across all processed accounts must be kept under a maximum limit of 1% of total bills prepared. | 1% Max Error | The overall error rate across all prepared bills must remain under the 1% cap. | N/A | No | N/A | Reported data not available.
2023-24 | Billing Complaints | Billing Disputes (No inspection) | Correcting billing errors where no additional on-site inspection or information is required. | When a billing complaint is raised and no on-site investigation is needed, the revised bill must be issued within 24 working hours. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2023-24 | Billing Complaints | Billing Disputes (LT - Inspection) | Correcting billing errors where inspection or meter verification is needed for Low Tension (LT) consumers. | If a billing complaint requires field inspection or meter checking for LT consumers, the licensee must issue the revised bill within 7 working days. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2023-24 | Billing Complaints | Billing Disputes (HT - Inspection) | Correcting billing errors where inspection or meter verification is needed for High Tension (HT) consumers. | For HT consumer billing disputes requiring on-site verification, the revised bill must be completed and issued within 15 days. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2023-24 | Metering Complaints | System Meter Health | The maximum allowable proportion of active meters that are malfunctioning or defective. | The utility must manage its network such that the overall proportion of faulty meters in service does not exceed 3% of the total meters. | 3% Max Defect | The overall percentage of faulty meters in service must be kept below the 3% ceiling. | N/A | No | N/A | Reported data not available.
2023-24 | Metering Complaints | Defective Meter Resolution (Urban) | Testing and replacing defective, creeping, or stuck meters in urban areas. | For defective meters in urban areas, the licensee must inspect them within 7 days and complete the replacement within 15 days thereafter. | 99 | At least 99% of cases in urban areas must be resolved within the specified timelines. | N/A | No | N/A | Reported data not available.
2023-24 | Metering Complaints | Defective Meter Resolution (Rural) | Testing and replacing defective, creeping, or stuck meters in rural areas. | The utility must inspect a reported defective meter in rural areas within 15 days and replace it within 15 days of that inspection. | 98 | At least 98% of cases in rural areas must be resolved within the specified timelines. | N/A | No | N/A | Reported data not available.
2023-24 | Metering Complaints | Burnt Meter (Licensee Cause) | Replacing burnt meters due to network failures (such as high voltage or loose contacts). | When a meter burns out due to utility-attributable factors, it must be replaced at licensee cost within 7 days. | 99% (U) / 98% (R) | At least 99% of urban and 98% of rural complaints must be resolved within the standard. | N/A | No | N/A | Reported data not available.
2023-24 | Metering Complaints | Burnt Meter (Consumer Cause) | Replacing burnt meters due to consumer overloading, tampering, or water exposure. | If a meter is burnt due to consumer-side issues, the licensee must replace it within 14 days of receiving payment or a replacement meter. | 99% (U) / 98% (R) | At least 99% of urban and 98% of rural complaints must be resolved within the standard. | N/A | No | N/A | Reported data not available.
2023-24 | Voltage Issues | Voltage Unbalance | Limit on the symmetry deviation among phase voltages at the point of supply. | The phase voltage unbalance at the consumer's point of supply must be maintained so that it does not exceed 3%. | 98 | At least 98% of cases related to voltage unbalance must be resolved. | N/A | No | N/A | Reported data not available.
2023-24 | Voltage Issues | Voltage Fluctuations (No network expansion) | Resolving voltage issues where system network expansion is not required. | The licensee must resolve complaints regarding voltage levels within 10 days when no network expansion is required. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2023-24 | Voltage Issues | Voltage Fluctuations (System Upgrade) | Resolving voltage issues where system capacity reinforcement or upgrade is required. | Where resolving voltage fluctuations requires system up-gradation or network enhancement, the works must be completed within 120 days. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2023-24 | Voltage Issues | Voltage Fluctuations (Substation Erection) | Resolving voltage issues when a new substation needs to be erected. | When resolving a voltage issue requires erecting a new substation, the utility must complete it within the time period approved by the Commission. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2023-24 | New Connections / Load Changes | Feasible Connection (Existing network) | Releasing supply where distribution mains are already in place. | The distribution licensee must release a new electricity connection within 30 days of receiving a completed application and requisite charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2023-24 | New Connections / Load Changes | Low Tension (LT) Network Expansion | Releasing LT supply when distribution main extension is required. | Where an LT connection requires expanding or enhancing the distribution network, the supply must be released within 30 days of receiving payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2023-24 | New Connections / Load Changes | High Tension (HT) Connection - 11 KV | Releasing 11 KV supply when network extension is required. | The licensee must complete the necessary 11 KV network expansion and release supply within 60 days of payment of prescribed charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2023-24 | New Connections / Load Changes | High Tension (HT) Connection - 33 KV | Releasing 33 KV supply when network extension is required. | For new HT 33 KV connections requiring network extension, the licensee must complete the work and release supply within 90 days of payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2023-24 | New Connections / Load Changes | Extra High Tension (EHT) Connection | Releasing EHT supply when network extension is required. | When releasing an Extra High Tension supply involves network extension, the connection must be completed and energized within 180 days of payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2023-24 | New Connections / Load Changes | Substation Erection | Releasing supply when a new substation must be erected. | If releasing a new connection requires erecting a substation, the licensee must complete the installation within the timeframe approved by the Commission. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2023-24 | Consumer Service Alterations | Title Transfer | Processing the transfer of ownership of a service connection to a new owner. | The licensee must process and finalize the transfer of connection ownership within 7 days of receiving the documents and prescribed fee. | 98 | At least 98% of cases related to title transfer must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
2023-24 | Consumer Service Alterations | Category Conversion | Processing the change of consumer/tariff category. | A request for tariff or category conversion must be processed and completed by the licensee within 7 days of receiving the required documents. | 98 | At least 98% of cases related to conversion must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
2023-24 | Consumer Service Alterations | Load Reduction | Processing a consumer's request to reduce contract demand. | The licensee must complete the load reduction process within the notice period specified in the Electricity Supply Code. | 98 | At least 98% of load reduction requests must be completed within the notice period. | N/A | No | N/A | Reported data not available.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Restoration of Power Supply | Normal Fuse-off Calls (Urban) | Replacing blown Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | The distribution licensee must replace blown fuses and restore power supply within 4 hours in cities and towns. | 95 | At least 95% of calls received must be rectified within the specified time limit. | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Normal Fuse-off Calls (Rural) | Replacing blown Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | In rural areas, the licensee is mandated to replace blown fuses and restore the supply within 24 hours. | 95 | At least 95% of calls received must be rectified within the specified time limit. | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Overhead Line / Cable Breakdowns (Urban) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | For overhead line or cable failures in cities and towns, the utility must resolve the breakdown and restore electricity within 6 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Overhead Line / Cable Breakdowns (Rural) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | Power supply restoration following an overhead line or cable breakdown in rural areas must be completed within 36 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Underground Cable Breakdowns (Urban) | Locating, repairing, and re-energising the system following faults in underground cables. | The licensee is required to locate, repair, and re-energize the network within 24 hours of an underground cable fault in urban areas. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Underground Cable Breakdowns (Rural) | Locating, repairing, and re-energising the system following faults in underground cables. | Underground cable faults in rural areas must be located and fully repaired to restore supply within 48 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Distribution Transformer Failure (Urban) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | The utility must replace or repair a failed distribution transformer and restore supply to consumers within 24 hours in urban areas. | 95 | At least 95% of failed transformers must be replaced within the specified time limit. | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Power Supply | Distribution Transformer Failure (Rural) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | Following a distribution transformer failure in rural areas, the company must complete replacement and restore supply within 72 hours. | 95 | At least 95% of failed transformers must be replaced within the specified time limit. | N/A | No | N/A | Reported data not available.
2024-25 | System Outages | Scheduled Outages (Duration) | Pre-arranged shut-downs of equipment and lines for necessary maintenance work. | The maximum duration of a pre-planned maintenance outage is strictly capped at 12 hours in a single stretch. | 95 | At least 95% of scheduled outages must comply with the maximum duration standard. | N/A | No | N/A | Reported data not available.
2024-25 | System Outages | Scheduled Outages (Restoration) | Pre-arranged shut-downs of equipment and lines for necessary maintenance work. | During pre-arranged maintenance, the utility must ensure power supply is fully restored not later than 6:00 PM. | 95 | At least 95% of planned outages must have supply restored by 6:00 PM. | N/A | No | N/A | Reported data not available.
2024-25 | Street Light Complaints | Street Light Faults | Rectification of line faults and replacement of public street lighting fixtures. | The licensee must rectify line faults or replace fused and defective public street lighting fixtures as soon as possible. | 90 | At least 90% of street light complaints must be resolved. | N/A | No | N/A | Reported data not available.
2024-25 | Billing Complaints | Billing Accuracy | Total allowable rate of billing errors across all prepared accounts. | The total number of billing mistakes across all processed accounts must be kept under a maximum limit of 1% of total bills prepared. | 1% Max Error | The overall error rate across all prepared bills must remain under the 1% cap. | N/A | No | N/A | Reported data not available.
2024-25 | Billing Complaints | Billing Disputes (No inspection) | Correcting billing errors where no additional on-site inspection or information is required. | When a billing complaint is raised and no on-site investigation is needed, the revised bill must be issued within 24 working hours. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2024-25 | Billing Complaints | Billing Disputes (LT - Inspection) | Correcting billing errors where inspection or meter verification is needed for Low Tension (LT) consumers. | If a billing complaint requires field inspection or meter checking for LT consumers, the licensee must issue the revised bill within 7 working days. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2024-25 | Billing Complaints | Billing Disputes (HT - Inspection) | Correcting billing errors where inspection or meter verification is needed for High Tension (HT) consumers. | For HT consumer billing disputes requiring on-site verification, the revised bill must be completed and issued within 15 days. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2024-25 | Metering Complaints | System Meter Health | The maximum allowable proportion of active meters that are malfunctioning or defective. | The utility must manage its network such that the overall proportion of faulty meters in service does not exceed 3% of the total meters. | 3% Max Defect | The overall percentage of faulty meters in service must be kept below the 3% ceiling. | N/A | No | N/A | Reported data not available.
2024-25 | Metering Complaints | Defective Meter Resolution (Urban) | Testing and replacing defective, creeping, or stuck meters in urban areas. | For defective meters in urban areas, the licensee must inspect them within 7 days and complete the replacement within 15 days thereafter. | 99 | At least 99% of cases in urban areas must be resolved within the specified timelines. | N/A | No | N/A | Reported data not available.
2024-25 | Metering Complaints | Defective Meter Resolution (Rural) | Testing and replacing defective, creeping, or stuck meters in rural areas. | The utility must inspect a reported defective meter in rural areas within 15 days and replace it within 15 days of that inspection. | 98 | At least 98% of cases in rural areas must be resolved within the specified timelines. | N/A | No | N/A | Reported data not available.
2024-25 | Metering Complaints | Burnt Meter (Licensee Cause) | Replacing burnt meters due to network failures (such as high voltage or loose contacts). | When a meter burns out due to utility-attributable factors, it must be replaced at licensee cost within 7 days. | 99% (U) / 98% (R) | At least 99% of urban and 98% of rural complaints must be resolved within the standard. | N/A | No | N/A | Reported data not available.
2024-25 | Metering Complaints | Burnt Meter (Consumer Cause) | Replacing burnt meters due to consumer overloading, tampering, or water exposure. | If a meter is burnt due to consumer-side issues, the licensee must replace it within 14 days of receiving payment or a replacement meter. | 99% (U) / 98% (R) | At least 99% of urban and 98% of rural complaints must be resolved within the standard. | N/A | No | N/A | Reported data not available.
2024-25 | Voltage Issues | Voltage Unbalance | Limit on the symmetry deviation among phase voltages at the point of supply. | The phase voltage unbalance at the consumer's point of supply must be maintained so that it does not exceed 3%. | 98 | At least 98% of cases related to voltage unbalance must be resolved. | N/A | No | N/A | Reported data not available.
2024-25 | Voltage Issues | Voltage Fluctuations (No network expansion) | Resolving voltage issues where system network expansion is not required. | The licensee must resolve complaints regarding voltage levels within 10 days when no network expansion is required. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2024-25 | Voltage Issues | Voltage Fluctuations (System Upgrade) | Resolving voltage issues where system capacity reinforcement or upgrade is required. | Where resolving voltage fluctuations requires system up-gradation or network enhancement, the works must be completed within 120 days. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2024-25 | Voltage Issues | Voltage Fluctuations (Substation Erection) | Resolving voltage issues when a new substation needs to be erected. | When resolving a voltage issue requires erecting a new substation, the utility must complete it within the time period approved by the Commission. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2024-25 | New Connections / Load Changes | Feasible Connection (Existing network) | Releasing supply where distribution mains are already in place. | The distribution licensee must release a new electricity connection within 30 days of receiving a completed application and requisite charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2024-25 | New Connections / Load Changes | Low Tension (LT) Network Expansion | Releasing LT supply when distribution main extension is required. | Where an LT connection requires expanding or enhancing the distribution network, the supply must be released within 30 days of receiving payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2024-25 | New Connections / Load Changes | High Tension (HT) Connection - 11 KV | Releasing 11 KV supply when network extension is required. | The licensee must complete the necessary 11 KV network expansion and release supply within 60 days of payment of prescribed charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2024-25 | New Connections / Load Changes | High Tension (HT) Connection - 33 KV | Releasing 33 KV supply when network extension is required. | For new HT 33 KV connections requiring network extension, the licensee must complete the work and release supply within 90 days of payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2024-25 | New Connections / Load Changes | Extra High Tension (EHT) Connection | Releasing EHT supply when network extension is required. | When releasing an Extra High Tension supply involves network extension, the connection must be completed and energized within 180 days of payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2024-25 | New Connections / Load Changes | Substation Erection | Releasing supply when a new substation must be erected. | If releasing a new connection requires erecting a substation, the licensee must complete the installation within the timeframe approved by the Commission. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2024-25 | Consumer Service Alterations | Title Transfer | Processing the transfer of ownership of a service connection to a new owner. | The licensee must process and finalize the transfer of connection ownership within 7 days of receiving the documents and prescribed fee. | 98 | At least 98% of cases related to title transfer must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
2024-25 | Consumer Service Alterations | Category Conversion | Processing the change of consumer/tariff category. | A request for tariff or category conversion must be processed and completed by the licensee within 7 days of receiving the required documents. | 98 | At least 98% of cases related to conversion must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
2024-25 | Consumer Service Alterations | Load Reduction | Processing a consumer's request to reduce contract demand. | The licensee must complete the load reduction process within the notice period specified in the Electricity Supply Code. | 98 | At least 98% of load reduction requests must be completed within the notice period. | N/A | No | N/A | Reported data not available.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Restoration of Power Supply | Normal Fuse-off Calls (Urban) | Replacing blown Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | The distribution licensee must replace blown fuses and restore power supply within 4 hours in cities and towns. | 95 | At least 95% of calls received must be rectified within the specified time limit. | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Normal Fuse-off Calls (Rural) | Replacing blown Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | In rural areas, the licensee is mandated to replace blown fuses and restore the supply within 24 hours. | 95 | At least 95% of calls received must be rectified within the specified time limit. | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Overhead Line / Cable Breakdowns (Urban) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | For overhead line or cable failures in cities and towns, the utility must resolve the breakdown and restore electricity within 6 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Overhead Line / Cable Breakdowns (Rural) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | Power supply restoration following an overhead line or cable breakdown in rural areas must be completed within 36 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Underground Cable Breakdowns (Urban) | Locating, repairing, and re-energising the system following faults in underground cables. | The licensee is required to locate, repair, and re-energize the network within 24 hours of an underground cable fault in urban areas. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Underground Cable Breakdowns (Rural) | Locating, repairing, and re-energising the system following faults in underground cables. | Underground cable faults in rural areas must be located and fully repaired to restore supply within 48 hours. | 95 | At least 95% of cases must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Distribution Transformer Failure (Urban) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | The utility must replace or repair a failed distribution transformer and restore supply to consumers within 24 hours in urban areas. | 95 | At least 95% of failed transformers must be replaced within the specified time limit. | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Power Supply | Distribution Transformer Failure (Rural) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | Following a distribution transformer failure in rural areas, the company must complete replacement and restore supply within 72 hours. | 95 | At least 95% of failed transformers must be replaced within the specified time limit. | N/A | No | N/A | Reported data not available.
2025-26 | System Outages | Scheduled Outages (Duration) | Pre-arranged shut-downs of equipment and lines for necessary maintenance work. | The maximum duration of a pre-planned maintenance outage is strictly capped at 12 hours in a single stretch. | 95 | At least 95% of scheduled outages must comply with the maximum duration standard. | N/A | No | N/A | Reported data not available.
2025-26 | System Outages | Scheduled Outages (Restoration) | Pre-arranged shut-downs of equipment and lines for necessary maintenance work. | During pre-arranged maintenance, the utility must ensure power supply is fully restored not later than 6:00 PM. | 95 | At least 95% of planned outages must have supply restored by 6:00 PM. | N/A | No | N/A | Reported data not available.
2025-26 | Street Light Complaints | Street Light Faults | Rectification of line faults and replacement of public street lighting fixtures. | The licensee must rectify line faults or replace fused and defective public street lighting fixtures as soon as possible. | 90 | At least 90% of street light complaints must be resolved. | N/A | No | N/A | Reported data not available.
2025-26 | Billing Complaints | Billing Accuracy | Total allowable rate of billing errors across all prepared accounts. | The total number of billing mistakes across all processed accounts must be kept under a maximum limit of 1% of total bills prepared. | 1% Max Error | The overall error rate across all prepared bills must remain under the 1% cap. | N/A | No | N/A | Reported data not available.
2025-26 | Billing Complaints | Billing Disputes (No inspection) | Correcting billing errors where no additional on-site inspection or information is required. | When a billing complaint is raised and no on-site investigation is needed, the revised bill must be issued within 24 working hours. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2025-26 | Billing Complaints | Billing Disputes (LT - Inspection) | Correcting billing errors where inspection or meter verification is needed for Low Tension (LT) consumers. | If a billing complaint requires field inspection or meter checking for LT consumers, the licensee must issue the revised bill within 7 working days. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2025-26 | Billing Complaints | Billing Disputes (HT - Inspection) | Correcting billing errors where inspection or meter verification is needed for High Tension (HT) consumers. | For HT consumer billing disputes requiring on-site verification, the revised bill must be completed and issued within 15 days. | 99 | At least 99% of complaints must be resolved within the specified time limit. | N/A | No | N/A | Reported data not available.
2025-26 | Metering Complaints | System Meter Health | The maximum allowable proportion of active meters that are malfunctioning or defective. | The utility must manage its network such that the overall proportion of faulty meters in service does not exceed 3% of the total meters. | 3% Max Defect | The overall percentage of faulty meters in service must be kept below the 3% ceiling. | N/A | No | N/A | Reported data not available.
2025-26 | Metering Complaints | Defective Meter Resolution (Urban) | Testing and replacing defective, creeping, or stuck meters in urban areas. | For defective meters in urban areas, the licensee must inspect them within 7 days and complete the replacement within 15 days thereafter. | 99 | At least 99% of cases in urban areas must be resolved within the specified timelines. | N/A | No | N/A | Reported data not available.
2025-26 | Metering Complaints | Defective Meter Resolution (Rural) | Testing and replacing defective, creeping, or stuck meters in rural areas. | The utility must inspect a reported defective meter in rural areas within 15 days and replace it within 15 days of that inspection. | 98 | At least 98% of cases in rural areas must be resolved within the specified timelines. | N/A | No | N/A | Reported data not available.
2025-26 | Metering Complaints | Burnt Meter (Licensee Cause) | Replacing burnt meters due to network failures (such as high voltage or loose contacts). | When a meter burns out due to utility-attributable factors, it must be replaced at licensee cost within 7 days. | 99% (U) / 98% (R) | At least 99% of urban and 98% of rural complaints must be resolved within the standard. | N/A | No | N/A | Reported data not available.
2025-26 | Metering Complaints | Burnt Meter (Consumer Cause) | Replacing burnt meters due to consumer overloading, tampering, or water exposure. | If a meter is burnt due to consumer-side issues, the licensee must replace it within 14 days of receiving payment or a replacement meter. | 99% (U) / 98% (R) | At least 99% of urban and 98% of rural complaints must be resolved within the standard. | N/A | No | N/A | Reported data not available.
2025-26 | Voltage Issues | Voltage Unbalance | Limit on the symmetry deviation among phase voltages at the point of supply. | The phase voltage unbalance at the consumer's point of supply must be maintained so that it does not exceed 3%. | 98 | At least 98% of cases related to voltage unbalance must be resolved. | N/A | No | N/A | Reported data not available.
2025-26 | Voltage Issues | Voltage Fluctuations (No network expansion) | Resolving voltage issues where system network expansion is not required. | The licensee must resolve complaints regarding voltage levels within 10 days when no network expansion is required. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2025-26 | Voltage Issues | Voltage Fluctuations (System Upgrade) | Resolving voltage issues where system capacity reinforcement or upgrade is required. | Where resolving voltage fluctuations requires system up-gradation or network enhancement, the works must be completed within 120 days. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2025-26 | Voltage Issues | Voltage Fluctuations (Substation Erection) | Resolving voltage issues when a new substation needs to be erected. | When resolving a voltage issue requires erecting a new substation, the utility must complete it within the time period approved by the Commission. | 98 | At least 98% of voltage fluctuation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
2025-26 | New Connections / Load Changes | Feasible Connection (Existing network) | Releasing supply where distribution mains are already in place. | The distribution licensee must release a new electricity connection within 30 days of receiving a completed application and requisite charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2025-26 | New Connections / Load Changes | Low Tension (LT) Network Expansion | Releasing LT supply when distribution main extension is required. | Where an LT connection requires expanding or enhancing the distribution network, the supply must be released within 30 days of receiving payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2025-26 | New Connections / Load Changes | High Tension (HT) Connection - 11 KV | Releasing 11 KV supply when network extension is required. | The licensee must complete the necessary 11 KV network expansion and release supply within 60 days of payment of prescribed charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2025-26 | New Connections / Load Changes | High Tension (HT) Connection - 33 KV | Releasing 33 KV supply when network extension is required. | For new HT 33 KV connections requiring network extension, the licensee must complete the work and release supply within 90 days of payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2025-26 | New Connections / Load Changes | Extra High Tension (EHT) Connection | Releasing EHT supply when network extension is required. | When releasing an Extra High Tension supply involves network extension, the connection must be completed and energized within 180 days of payment. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2025-26 | New Connections / Load Changes | Substation Erection | Releasing supply when a new substation must be erected. | If releasing a new connection requires erecting a substation, the licensee must complete the installation within the timeframe approved by the Commission. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
2025-26 | Consumer Service Alterations | Title Transfer | Processing the transfer of ownership of a service connection to a new owner. | The licensee must process and finalize the transfer of connection ownership within 7 days of receiving the documents and prescribed fee. | 98 | At least 98% of cases related to title transfer must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
2025-26 | Consumer Service Alterations | Category Conversion | Processing the change of consumer/tariff category. | A request for tariff or category conversion must be processed and completed by the licensee within 7 days of receiving the required documents. | 98 | At least 98% of cases related to conversion must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
2025-26 | Consumer Service Alterations | Load Reduction | Processing a consumer's request to reduce contract demand. | The licensee must complete the load reduction process within the notice period specified in the Electricity Supply Code. | 98 | At least 98% of load reduction requests must be completed within the notice period. | N/A | No | N/A | Reported data not available.

## UP
Uttar Pradesh Electricity Regulatory Commission (Standards of Performance) Regulations, 2019
Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data | Comparison Possible? | Standard met? | If comparison not possible, why?
Restoration of Power Supply | Normal Fuse-off Calls (Class-I Cities) | Replacing blown fuses at distribution transformers or consumer premises. | The distribution licensee must replace blown fuses and restore power supply within 2 hours of receiving a complaint in Class-I Cities. | 95 | At least 95% of total fuse-off calls must be rectified within the specified time limits. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Normal Fuse-off Calls (Urban Areas) | Replacing blown fuses at distribution transformers or consumer premises. | The distribution licensee must replace blown fuses and restore power supply within 4 hours of receiving a complaint in Urban Areas. | 95 | At least 95% of total fuse-off calls must be rectified within the specified time limits. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Normal Fuse-off Calls (Rural Areas) | Replacing blown fuses at distribution transformers or consumer premises. | The distribution licensee must replace blown fuses and restore power supply within 6 hours of receiving a complaint in Rural Areas. | 95 | At least 95% of total fuse-off calls must be rectified within the specified time limits. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Overhead Line/Cable Breakdowns (Class-I Cities) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | The distribution licensee must resolve overhead line or cable breakdowns and restore supply within 2 hours of occurrence in Class-I Cities. | 95 | At least 95% of overall cases of line breakdowns must have power restored within specified limits. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Overhead Line/Cable Breakdowns (Urban Areas) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | The distribution licensee must resolve overhead line or cable breakdowns and restore supply within 3 hours of occurrence in Urban Areas. | 95 | At least 95% of overall cases of line breakdowns must have power restored within specified limits. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Overhead Line/Cable Breakdowns (Rural Areas) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | The distribution licensee must resolve overhead line or cable breakdowns and restore supply within 24 hours of occurrence in Rural Areas. | 95 | At least 95% of overall cases of line breakdowns must have power restored within specified limits. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Underground Cable Breakdowns (Class-I Cities & Urban Areas) | Locating, repairing, and re-energising the system following underground cable network faults. | The distribution licensee must locate, repair, and restore power supply within 12 hours of an underground cable breakdown in Class-I Cities and Urban Areas. | 95 | At least 95% of overall cases of line breakdowns must have power restored within specified limits. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Underground Cable Breakdowns (Rural Areas) | Locating, repairing, and re-energising the system following underground cable network faults. | The distribution licensee must locate, repair, and restore power supply within 48 hours of an underground cable breakdown in Rural Areas. | 95 | At least 95% of overall cases of line breakdowns must have power restored within specified limits. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Distribution Transformer Failure (Class-I Cities) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | The distribution licensee must replace or repair a failed distribution transformer and restore supply within 6 hours of receiving a complaint in Class-I Cities. | 95 | At least 95% of total failed distribution transformers must be replaced within the specified time limits. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Distribution Transformer Failure (Urban Areas) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | The distribution licensee must replace or repair a failed distribution transformer and restore supply within 8 hours of receiving a complaint in Urban Areas. | 95 | At least 95% of total failed distribution transformers must be replaced within the specified time limits. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Distribution Transformer Failure (Rural Areas) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | The distribution licensee must replace or repair a failed distribution transformer and restore supply within 48 hours of receiving a complaint in Rural Areas. | 95 | At least 95% of total failed distribution transformers must be replaced within the specified time limits. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Reconnection of Supply (Disconnection for non-payment) | Restoring supply after disconnection due to non-payment, upon settlement of dues. | The distribution licensee must restore power supply to a consumer disconnected for non-payment within 2 hours of prepaid meter recharge. | 95 | At least 95% of reconnection of supply cases must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
System Outages | Scheduled Outages (Notification) | Advance notification of pre-planned outages for system maintenance. | The distribution licensee must notify consumers of any scheduled outages (excluding load-shedding) at least 24 hours in advance. | 95 | At least 95% of scheduled outages must comply with the advance notification standard. | N/A | No | N/A | Reported data not available.
System Outages | Scheduled Outages (Duration - Class-I & Urban) | Restricting duration of pre-planned maintenance shutdowns on 11kV feeders. | The distribution licensee must limit the total duration of scheduled outages to not exceed 12 hours in a month for any 11kV feeder in Class-I and Urban areas. | 95 | At least 95% of scheduled outages must comply with the monthly duration limits. | N/A | No | N/A | Reported data not available.
System Outages | Scheduled Outages (Duration - Rural) | Restricting duration of pre-planned maintenance shutdowns on 11kV feeders. | The distribution licensee must limit the total duration of scheduled outages to not exceed 24 hours in a month for any 11kV feeder in Rural Areas. | 95 | At least 95% of scheduled outages must comply with the monthly duration limits. | N/A | No | N/A | Reported data not available.
Shifting of Service Connection | Shifting of Meters/Service Lines (Cost Estimation - Class-I) | Inspecting and informing the consumer of estimated shifting costs. | The distribution licensee must inspect and inform the estimated cost to the consumer within 7 days of receiving the shifting application in Class-I Cities. | 95 | At least 95% of shifting requests must comply with the inspection and estimation timeline. | N/A | No | N/A | Reported data not available.
Shifting of Service Connection | Shifting of Meters/Service Lines (Cost Estimation - Urban) | Inspecting and informing the consumer of estimated shifting costs. | The distribution licensee must inspect and inform the estimated cost to the consumer within 10 days of receiving the shifting application in Urban Areas. | 95 | At least 95% of shifting requests must comply with the inspection and estimation timeline. | N/A | No | N/A | Reported data not available.
Shifting of Service Connection | Shifting of Meters/Service Lines (Cost Estimation - Rural) | Inspecting and informing the consumer of estimated shifting costs. | The distribution licensee must inspect and inform the estimated cost to the consumer within 15 days of receiving the shifting application in Rural Areas. | 95 | At least 95% of shifting requests must comply with the inspection and estimation timeline. | N/A | No | N/A | Reported data not available.
Shifting of Service Connection | Shifting of Meters/Service Lines (Work Completion) | Physically shifting the meter or service line after payments and clearances. | The distribution licensee must complete the physical shifting of the meter or service line within 7 days from the date of payment and clearances. | 95 | At least 95% of shifting requests must be fully executed within the specified work schedule. | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | New Connections & Load Alterations | Processing applications and releasing supply under the Electricity Supply Code. | The distribution licensee must release new connections, enhance load, or reduce contracted load as per the provisions of the UPERC Electricity Supply Code. | 95 | At least 95% of connection and load change cases must be processed within the Supply Code limits. | N/A | No | N/A | Reported data not available.
Consumer Service Alterations | Transfer of Ownership (Title Transfer) | Transferring the electricity account title to a new owner. | The distribution licensee must execute and complete the transfer of ownership of a service connection within the second billing cycle from receipt of application. | 95 | At least 95% of ownership transfer cases must be resolved within the specified billing cycles. | N/A | No | N/A | Reported data not available.
Consumer Service Alterations | Change of Category (Conversion of Service) | Changing consumer or tariff categories (e.g., converting phases or voltage levels). | The distribution licensee must convert the service connection phase or voltage level within the second billing cycle from payment of necessary charges. | 95 | At least 95% of category change cases must be resolved within the specified billing cycles. | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | Temporary Supply of Power | Providing electricity supply for temporary periods. | The distribution licensee must provide temporary supply of power as per Section 4.10 of the UPERC Electricity Supply Code. | 95 | At least 95% of temporary supply cases must be provided within the specified timelines. | N/A | No | N/A | Reported data not available.
Consumer Service Alterations | Disconnection of Supply (Permanent) | Processing requests for permanent service disconnection. | The distribution licensee must execute requests for permanent disconnection as per Section 4.38 of the UPERC Electricity Supply Code. | 95 | At least 95% of permanent disconnection requests must be processed within the Supply Code limits. | N/A | No | N/A | Reported data not available.
Metering Complaints | System Meter Health | Maintaining overall meter health across the distribution system. | The distribution licensee must maintain the percentage of defective meters in service at a value not greater than 3% of the total meters in service. | 3 | The overall percentage of faulty or defective active meters across the network must not exceed the 3% cap. | N/A | No | N/A | Reported data not available.
Billing Complaints | Billing Mistakes (System Error Rate) | Managing the error rate of issued bills requiring modifications. | The distribution licensee must limit the percentage of bills requiring modifications following complaints to not exceed 0.1% of the total bills issued. | 0.1 | The overall billing error rate requiring corrections must remain under the 0.1% ceiling. | N/A | No | N/A | Reported data not available.
Load Shedding | Power Shortage Notification | Advance announcement of power cuts or load shedding schedules. | The distribution licensee must submit its load shedding plan to the Commission for approval and publish it in the newspaper at least 48 hours in advance. | 100 | The licensee must fully comply with the advance approval and 48-hour newspaper publication standard. | N/A | No | N/A | Reported data not available.
Power Supply Hours | Power Supply Reliability | Meeting target duration of electricity supply to consumers. | The distribution licensee must achieve the standard of performance in at least 96% against the scheduled hours of power supply. | 96 | At least 96% of the scheduled hours of power supply must be successfully met and maintained. | N/A | No | N/A | Reported data not available.

## TAMIL NADU
Tamil Nadu Generation and Distribution Corporation Limited
TAMIL NADU ELECTRICITY DISTRIBUTION STANDARDS OF PERFORMANCE REGULATIONS, 2004 (As amended upto 31-03-2024)
Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data | Comparison Possible? | Standard met? | If comparison not possible, why?
Restoration of Power Supply | HT Supply Failure (Corporation Urban) | Restoring power supply after a High Tension (HT) grid or line failure in Corporation limits. | The distribution licensee must restore power supply following a High Tension (HT) supply failure within 1 hour in Corporation limits (available round-the-clock). | 75 | At least 75% of cases must be resolved within the standard; 20% of the remaining cases must be resolved within 24 hours of the complaint. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | HT Supply Failure (Municipalities) | Restoring power supply after a High Tension (HT) grid or line failure in Municipal areas. | The distribution licensee must restore power supply following a High Tension (HT) supply failure within 3 hours in Municipality areas. | 75 | At least 75% of cases must be resolved within the standard; 20% of the remaining cases must be resolved within 24 hours of the complaint. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | HT Supply Failure (Rural Areas) | Restoring power supply after a High Tension (HT) grid or line failure in rural villages and agricultural networks. | The distribution licensee must restore power supply following a High Tension (HT) supply failure within 6 hours in rural areas. | 75 | At least 75% of cases must be resolved within the standard; 20% of the remaining cases must be resolved within 24 hours of the complaint. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | HT Supply Failure (Hill Areas) | Restoring power supply after a High Tension (HT) grid or line failure in mountainous or hilly terrain. | The distribution licensee must restore power supply following a High Tension (HT) supply failure within 12 hours in hilly areas. | 75 | At least 75% of cases must be resolved within the standard; 20% of the remaining cases must be resolved within 24 hours of the complaint. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Fault in Transformer Structure, LT Line, or Pillar Box (Corporation Urban) | Restoring supply after Low Tension line faults, distribution pillar box defects, or structural faults. | The distribution licensee must resolve the fault in the transformer structure, LT line, or pillar box and restore power within 2 hours in Corporation limits (available round-the-clock). | 75 | At least 75% of cases must be resolved within the standard; 20% of the remaining cases must be resolved within 24 hours of the complaint. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Fault in Transformer Structure, LT Line, or Pillar Box (Municipalities) | Restoring supply after Low Tension line faults, distribution pillar box defects, or structural faults. | The distribution licensee must resolve the fault in the transformer structure, LT line, or pillar box and restore power within 4 hours in Municipalities. | 75 | At least 75% of cases must be resolved within the standard; 20% of the remaining cases must be resolved within 24 hours of the complaint. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Fault in Transformer Structure, LT Line, or Pillar Box (Rural Areas) | Restoring supply after Low Tension line faults, distribution pillar box defects, or structural faults. | The distribution licensee must resolve the fault in the transformer structure, LT line, or pillar box and restore power within 6 hours in Rural Areas. | 75 | At least 75% of cases must be resolved within the standard; 20% of the remaining cases must be resolved within 24 hours of the complaint. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Fault in Transformer Structure, LT Line, or Pillar Box (Hill Areas) | Restoring supply after Low Tension line faults, distribution pillar box defects, or structural faults. | The distribution licensee must resolve the fault in the transformer structure, LT line, or pillar box and restore power within 12 hours in Hill Areas. | 75 | At least 75% of cases must be resolved within the standard; 20% of the remaining cases must be resolved within 24 hours of the complaint. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Distribution Transformer Failure (Corporation Urban) | Replacing or repairing failed distribution transformers on the urban network. | The distribution licensee must replace or repair a failed distribution transformer and restore supply within 24 hours in Corporation limits. | 95 | At least 95% of failed distribution transformers must be replaced within the specified time limit. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Distribution Transformer Failure (Municipalities / Rural / Hill) | Replacing or repairing failed distribution transformers on the municipal, rural, or hill network. | The distribution licensee must replace or repair a failed distribution transformer and restore supply within 48 hours in Municipalities, Rural, or Hill areas. | 95 | At least 95% of failed distribution transformers must be replaced within the specified time limit. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Individual Service Connection Fault (Corporation Urban) | Resolving specific consumer service connection faults (fuses, service line drops). | The distribution licensee must resolve an individual service connection fault within 3 hours in Corporation limits (round-the-clock). | 75 | At least 75% of cases must be resolved within the standard; 20% of the remaining cases must be resolved within 24 hours of the complaint. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Individual Service Connection Fault (Municipalities) | Resolving specific consumer service connection faults (fuses, service line drops). | The distribution licensee must resolve an individual service connection fault within 9 hours in Municipalities. | 75% | At least 75% of cases must be resolved within the standard; 20% of the remaining cases must be resolved within 24 hours of the complaint. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Individual Service Connection Fault (Rural Areas) | Resolving specific consumer service connection faults (fuses, service line drops). | The distribution licensee must resolve an individual service connection fault within 12 hours in Rural Areas (excluding the night hours from 6:00 PM to 8:00 AM). | 75 | At least 75% of cases must be resolved within the standard; 20% of the remaining cases must be resolved within 24 hours of the complaint. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Individual Service Connection Fault (Hill Areas) | Resolving specific consumer service connection faults (fuses, service line drops). | The distribution licensee must resolve an individual service connection fault within 24 hours in Hill Areas. | 75 | At least 75% of cases must be resolved within the standard; 20% of the remaining cases must be resolved within 24 hours of the complaint. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Reconnection of Supply | Restoring power supply to a disconnected service connection following payment of dues. | The distribution licensee must restore the supply to a disconnected service connection immediately and in any case not exceeding 6 working hours after the receipt of electricity charges and dues. | 100 | The performance level is expected to be maintained at 100% of cases. | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | LT Connection (No extension/improvement) | Releasing new Low Tension (LT) service connection where existing distribution mains require no extension or improvement. | The distribution licensee must give supply of electricity within 7 days (preferably within 3 days) of receiving a completed application requiring such supply. | 95 | At least 95% of connections must be released within the specified time schedule. | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | LT Connection (Involving network extension without DTR) | Releasing new LT service connection where distribution mains extension is required but no new distribution transformer is needed. | The distribution licensee must complete the network extension and release the connection within 60 days of receiving completed application/payments. | 95 | At least 95% of connections must be released within the specified time schedule. | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | LT Connection (Involving network extension with DTR) | Releasing new LT service connection where distribution mains extension as well as commissioning of a new distribution transformer is required. | The distribution licensee must complete the transformer installation and release the connection within 90 days of receiving payments. | 95 | At least 95% of connections must be released within the specified time schedule. | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | HT / EHT Connection (Involving Extension & Improvement) | Releasing HT or EHT connection requiring network extension and improvements. | The distribution licensee must complete HT extension within 60 days and EHT extension within 150 days of receiving payments. | 95 | At least 95% of connections must be released within the specified time schedule. | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | HT / EHT Connection (Involving Power Transformer enhancement) | Releasing HT or EHT connection requiring addition or capacity enhancement of power transformers. | The distribution licensee must complete power transformer addition/enhancement and release HT connection within 120 days and EHT connection within 180 days. | 95 | At least 95% of connections must be released within the specified time schedule. | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | HT / EHT Connection (Involving New Substation Commissioning) | Releasing HT or EHT connection requiring the construction and commissioning of a new substation. | The distribution licensee must commission a new substation and release HT connection within 270 days and EHT connection within 365 days. | 95 | At least 95% of connections must be released within the specified time schedule. | N/A | No | N/A | Reported data not available.
Temporary Supply | Temporary Connection purely for Temporary Purposes (No system augmentation) | Providing supply for temporary purposes like circus, events, festivals, or illumination where no system augmentation is needed. | The distribution licensee must provide temporary supply purely for temporary purposes not later than 48 hours where no system augmentation is required. | 95 | At least 95% of temporary connections must be released within the specified limits. | N/A | No | N/A | Reported data not available.
Temporary Supply | Refund of Balance Deposit in Temporary Supply (Service Transfer) | Processing the refund or transfer of balance deposits on expiry of the temporary supply. | The distribution licensee must transfer the balance temporary supply deposit to another active service within 7 days of receiving the consumer's option or disconnection. | 90 | At least 90% of deposit refund cases must be completed within the specified timelines. | N/A | No | N/A | Reported data not available.
Temporary Supply | Refund of Balance Deposit in Temporary Supply (Bank Refund) | Processing the refund or transfer of balance deposits on expiry of the temporary supply. | The distribution licensee must refund the balance temporary supply deposit to the consumer's bank account within 7 days of disconnection or receiving bank details. | 90 | At least 90% of deposit refund cases must be completed within the specified timelines. | N/A | No | N/A | Reported data not available.
Shifting of Service | Shifting of Meter or Service Line | Shifting the meter or service line within consumer premises at the consumer's cost. | The distribution licensee must complete the physical shifting of the meter or service connection within 25 days of receipt of payment and charges. | 90 | At least 90% of shifting requests must be resolved within the specified timeline. (Regulation 23(5) cites 95%, Appendix target cites 90%). | N/A | No | N/A | Reported data not available.
Shifting of Service | Shifting of LT / HT Lines | Deviation or shifting of LT or HT overhead distribution lines at the consumer's request and cost. | The distribution licensee must complete the shifting of HT or LT distribution lines within 60 days of receiving necessary expenses. | 90 | At least 90% of line shifting requests must be resolved within the specified timeline. (Regulation 23(5) cites 95%, Appendix target cites 90%). | N/A | No | N/A | Reported data not available.
Shifting of Service | Shifting of Transformer Structures | Relocating distribution transformer structures at the consumer's request and cost. | The distribution licensee must complete the physical relocation of distribution transformer structures within 90 days of receiving necessary payments. | 90 | At least 90% of shifting requests must be resolved within the specified timeline. (Regulation 23(5) cites 95%, Appendix target cites 90%). | N/A | No | N/A | Reported data not available.
Consumer Service Alterations | Transfer of Service Connection / Title Transfer | Processing the transfer of connection ownership to a new applicant. | The distribution licensee must effect the transfer of service connection within 7 days from the date of receipt of a complete application. | 95 | At least 95% of transfer of service connection requests must be completed within the timeline. | N/A | No | N/A | Reported data not available.
Consumer Service Alterations | Change of Tariff | Processing a request to change the consumer's tariff category. | The distribution licensee must effect the change of tariff within 7 working days from the date of receipt of application from the consumer. | 95 | At least 95% of change of tariff requests must be completed within the timeline. | N/A | No | N/A | Reported data not available.
Consumer Service Alterations | Permanent Reduction of Demand (No meter change) | Processing permanent demand/load reduction where no metering change is required. | The distribution licensee must effect the permanent reduction of demand within 7 days of receiving the request when no metering system change is needed. | 95 | At least 95% of load reduction requests must be completed within the timeline. | N/A | No | N/A | Reported data not available.
Consumer Service Alterations | Permanent Reduction of Demand (With meter change) | Processing permanent demand/load reduction where metering changes are required. | The distribution licensee must effect the permanent reduction of demand within 4 weeks of receiving the request when a change in the metering system is required. | 95 | At least 95% of load reduction requests must be completed within the timeline. | N/A | No | N/A | Reported data not available.
Consumer Service Alterations | Correction of Consumer Details | Correcting address, phone number, email ID, or other registration details. | The distribution licensee must update and correct consumer registration details within 7 days of receiving supporting documents. | 95 | At least 95% of consumer details updates must be completed within the timeline. | N/A | No | N/A | Reported data not available.
Billing Complaints | Billing Complaints Prior to Due Date | Resolving errors in bills before the due date for payment. | The distribution licensee must resolve any complaints in billing received prior to the due date before the next billing cycle, along with necessary adjustments. | 95 | At least 95% of billing complaints must be resolved within the timeline. | N/A | No | N/A | Reported data not available.
Billing Complaints | Arithmetic Billing Errors | Correcting simple arithmetic calculation errors in consumer accounts. | The distribution licensee must resolve arithmetic billing errors within the payment due date if the complaint is received at least 3 days prior to the due date. | 95 | At least 95% of billing complaints must be resolved within the timeline. | N/A | No | N/A | Reported data not available.
Metering Complaints | Defective or Burnt Meter Replacement | Testing and replacing faulty, non-functional, creeping, stuck, or burnt meters. | The distribution licensee must replace a malfunctioning, defective, or burnt meter within 7 days (non-availability of meters is not a valid reason for delay). | 95% | At least 95% of defective or burnt meter replacements must be completed within the specified timeline. | N/A | No | N/A | Reported data not available.
Voltage Issues | Quality of Supply Complaint | Conducting site visits and responding to power quality or voltage complaints in writing. | On receiving a quality of supply complaint, the licensee's representative must visit the site and convey proposing actions in writing within 10 days. | 90 | At least 90% of voltage fluctuation and quality complaints must be resolved within the specified benchmarks. | N/A | No | N/A | Reported data not available.
Voltage Issues | Voltage Rectification (No network expansion) | Resolving verified voltage variation complaints without system expansion. | The distribution licensee must resolve voltage fluctuation complaints within 48 hours where no network expansion or enhancement is involved. | 90 | At least 90% of voltage complaints must be rectified within the specified limits. | N/A | No | N/A | Reported data not available.
Voltage Issues | Voltage Rectification (LT upgrade / installation of capacitors) | Resolving verified voltage variation complaints with LT network upgrade. | The distribution licensee must resolve voltage fluctuation complaints within 60 days where up-gradation of the LT network, transformer, or capacitor installation is needed. | 90 | At least 90% of voltage complaints must be rectified within the specified limits. | N/A | No | N/A | Reported data not available.
Voltage Issues | Voltage Rectification (HT network upgrade) | Resolving verified voltage variation complaints with HT network upgrade. | The distribution licensee must resolve voltage fluctuation complaints within 120 days where up-gradation of the HT network is involved. | 90 | At least 90% of voltage complaints must be rectified within the specified limits. | N/A | No | N/A | Reported data not available.
Consumer Grievance Response | Responding to Written Grievances | Providing official responses to written letters sent by consumers to the Territorial Engineer. | The Territorial Engineer must send an initial reply within 10 days of receiving a consumer's letter and a complete substantive response within 20 days. | 90 | At least 90% of written consumer complaints must receive responses within these timelines. | N/A | No | N/A | Reported data not available.
Consumer Grievance Response | Making and Keeping Appointments | Keeping written appointments made to visit consumer premises. | The distribution licensee must keep written appointments or provide at least 24 hours' notice of cancellation to the consumer. | 95 | At least 95% of scheduled consumer appointments must be kept. | N/A | No | N/A | Reported data not available.
Consumer Grievance Response | Grievance Handling | Accepting and handling consumer complaints at scheduled grievance offices. | The distribution licensee's representative must receive complaints on appointed days and times, and provide compensation if cancellation is not communicated. | 100 | At least 100% of scheduled grievance handling sessions must comply with standards. | N/A | No | N/A | Reported data not available.

## KARNATAKA
Karnataka Electricity Regulatory Commission Licensees' Standards of Performance) Regulations - 2004 | Karnataka Electricity Regulatory Commission (Rights of Consumers Relating to Supply of Electricity, Standards of Performance (SoP) and allied matters) Regulations, 2022.
Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data | Comparison Possible? | Standard met? | If comparison not possible, why?
Restoration of Power Supply | Normal Fuse-off Calls (Cities & Towns) | Replacing blown Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | The distribution licensee must replace blown fuses and restore supply following normal fuse-off calls within 6 hours in Cities and Towns. | 99 | At least 99% of fuse-off call complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Normal Fuse-off Calls (Rural Areas) | Replacing blown Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | The distribution licensee must replace blown fuses and restore supply following normal fuse-off calls within 24 hours in Rural Areas. | 99 | At least 99% of fuse-off call complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Line Breakdowns (Cities & Towns) | Repairing overhead distribution lines or cables, excluding cases where poles are broken or uprooted. | The distribution licensee must resolve line breakdowns and restore supply within 6 hours in Cities and Towns (extended to 10 hours if poles are broken or uprooted). | 95 | At least 95% of line breakdowns must be rectified within the specified time limits. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Line Breakdowns (Rural Areas) | Repairing overhead distribution lines or cables, excluding cases where poles are broken or uprooted. | The distribution licensee must resolve line breakdowns and restore supply within 24 hours in all cases in Rural Areas. | 95 | At least 95% of line breakdowns must be rectified within the specified time limits. | N/A | No | N/A | Reported data not available.
System Interruptions | Frequency of Interruptions (Urban) | Restricting the number of scheduled or unscheduled power interruptions. | The distribution licensee must limit power interruptions (scheduled or unscheduled) to a maximum of 2 interruptions per consumer per day in Urban Areas (including NJY feeders). | 98 | At least 98% of days must comply with the daily interruption limit in Urban Areas. | N/A | No | N/A | Reported data not available.
System Interruptions | Frequency of Interruptions (Rural) | Restricting the number of scheduled or unscheduled power interruptions. | The distribution licensee must limit power interruptions (scheduled or unscheduled) to a maximum of 3 interruptions per consumer per day in Rural Areas. | 95 | At least 95% of days must comply with the daily interruption limit in Rural Areas. | N/A | No | N/A | Reported data not available.
System Interruptions | Duration of Interruptions (Urban) | Restricting the cumulative duration of scheduled or unscheduled outages. | The distribution licensee must limit the total duration of interruptions in a month to a maximum of 90 minutes in Urban Areas. | 98 | At least 98% of months must comply with the cumulative duration limit in Urban Areas. | N/A | No | N/A | Reported data not available.
System Interruptions | Duration of Interruptions (Rural) | Restricting the cumulative duration of scheduled or unscheduled outages. | The distribution licensee must limit the total duration of interruptions in a month to a maximum of 180 minutes in Rural Areas. | 95 | At least 95% of months must comply with the cumulative duration limit in Rural Areas. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Distribution Transformer Failure (Cities & Towns) | Replacing or repairing failed distribution transformers on the distribution network. | The distribution licensee must replace or repair a failed distribution transformer and restore supply within 24 hours in Cities and Towns. | 95 | At least 95% of transformer failures must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Distribution Transformer Failure (Rural Areas) | Replacing or repairing failed distribution transformers on the distribution network. | The distribution licensee must replace or repair a failed distribution transformer and restore supply within 72 hours in Rural Areas. | 95 | At least 95% of transformer failures must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
System Outages | Scheduled Outages (Duration) | Restricting pre-arranged shut-downs of equipment and lines for system maintenance. | The distribution licensee must limit the maximum duration of a scheduled maintenance outage to not exceed 12 hours in a single stretch. | 99 | At least 99% of scheduled outages must comply with the maximum duration limit. | N/A | No | N/A | Reported data not available.
System Outages | Scheduled Outages (Restoration) | Ensuring timely restoration of supply after pre-planned maintenance. | The distribution licensee must ensure power supply is fully restored by not later than 6:00 PM on any scheduled outage day. | 99 | At least 99% of scheduled outages must have supply restored by 6:00 PM. | N/A | No | N/A | Reported data not available.
Voltage Issues | Voltage Variations (No Network Expansion) | Resolving voltage fluctuation complaints where system expansion is not required. | The distribution licensee must resolve voltage level complaints within 7 days when no network expansion or enhancement is involved. | 95 | At least 95% of voltage variation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
Voltage Issues | Voltage Variations (System Upgrade) | Resolving voltage fluctuation complaints requiring network capacity enhancement. | Where resolving voltage variations requires up-gradation or enhancement of the distribution system, the works must be completed within 120 days. | 90 | At least 90% of voltage variation complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
Voltage Issues | Neutral Opening & Overvoltage (Cities) | Resolving issues of open neutral line and neutral-to-ground voltage deviations. | The distribution licensee must resolve open neutral issues and neutral voltage exceeding 2% of supply voltage within 6 hours in Cities. | 90 | At least 90% of open neutral complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
Voltage Issues | Neutral Opening & Overvoltage (Rural) | Resolving issues of open neutral line and neutral-to-ground voltage deviations. | The distribution licensee must resolve open neutral issues and neutral voltage exceeding 2% of supply voltage within 24 hours in Rural Areas. | 90 | At least 90% of open neutral complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
Metering Complaints | Inspect and Check Correctness of Meters | Verifying meter accuracy upon receiving consumer complaints. | The distribution licensee must inspect and verify the correctness of a disputed meter within 7 days of receiving the complaint. | 90 | At least 90% of meter inspection requests must be completed within the specified timeline. | N/A | No | N/A | Reported data not available.
Metering Complaints | Defective/Stuck Meter Replacement | Testing and replacing defective, creeping, MNR, or stuck meters. | The distribution licensee must replace defective, fast, slow, creeping, or stuck meters within 24 hours in Urban Areas and 72 hours in Rural Areas. | 90 | At least 90% of defective meter replacements must be completed within specified timelines. | N/A | No | N/A | Reported data not available.
Metering Complaints | Burnt Meter Replacement (Licensee Cause) | Replacing burnt meters where damage is due to system faults or utility error. | The distribution licensee must replace a burnt meter (if cause is not attributable to the consumer) within 24 hours in Urban Areas and 72 hours in Rural Areas. | 90 | At least 90% of burnt meter replacements must be completed within specified timelines. | N/A | No | N/A | Reported data not available.
Metering Complaints | Burnt Meter Replacement (Consumer Cause) | Replacing burnt meters where damage is due to overloading, tampering, etc. | The distribution licensee must replace a consumer-attributable burnt meter and restore supply within 24 hours in Urban Areas and 72 hours in Rural Areas after receiving payment of charges. | 95 | At least 95% of consumer-side burnt meter replacements must be completed within specified timelines. | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | Feasible Connection (Metro Cities) | Releasing new supply where the service is feasible from the existing network. | The distribution licensee must release a new service connection within 7 days of receiving a completed application in Metro Cities. | 95 | At least 95% of new connection requests must be serviced within the specified timelines. | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | Feasible Connection (Municipal Areas) | Releasing new supply where the service is feasible from the existing network. | The distribution licensee must release a new service connection within 15 days of receiving a completed application in Other Municipal Areas. | 95 | At least 95% of new connection requests must be serviced within the specified timelines. | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | Feasible Connection (Rural Areas) | Releasing new supply where the service is feasible from the existing network. | The distribution licensee must release a new service connection within 30 days of receiving a completed application in Rural Areas. | 95 | At least 95% of new connection requests must be serviced within the specified timelines. | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | Network Expansion (LT Connections) | Releasing LT supply where network enhancement or main extension is required. | Where LT connection requires distribution main extension, the licensee must release the supply within 45 days of receipt of application. | 95 | At least 95% of network-dependent LT connections must be released within 45 days. | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | Network Expansion (HT 11 KV Connections) | Releasing HT 11 KV supply where network expansion is required. | The distribution licensee must execute 11 KV network expansion and release supply within 60 days of receiving the application. | 95 | At least 95% of network-dependent HT 11 KV connections must be released within 60 days. | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | Network Expansion (HT 33 KV Connections) | Releasing HT 33 KV supply where network expansion is required. | The distribution licensee must execute 33 KV network expansion and release supply within 90 days of receiving the application. | 95 | At least 95% of network-dependent HT 33 KV connections must be released within 90 days. | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | Network Expansion (EHT Connections) | Releasing EHT supply where system expansion is required. | The distribution licensee must execute Extra High Tension (EHT) network expansion and release supply within 180 days of receiving the application. | 95 | At least 95% of EHT connection requests must be serviced within 180 days. | N/A | No | N/A | Reported data not available.
Consumer Service Alterations | Title Transfer & Category Changes | Transfer of ownership, category conversion, or title modifications. | The distribution licensee must process and complete title transfer of ownership or change of consumer category within 7 days of receiving the application. | 99 | At least 99% of administrative service alteration requests must be completed within 7 days. | N/A | No | N/A | Reported data not available.
Consumer Service Alterations | Disconnection on Consumer Request (Urban) | Executing service disconnections and physical line removals upon request. | The distribution licensee must execute service disconnection and line shifting within 2 days for LT installations and within 5 days for HT installations in Urban Areas. | 99 | At least 99% of consumer-initiated disconnection requests must be processed within specified timelines. | N/A | No | N/A | Reported data not available.
Consumer Service Alterations | Disconnection on Consumer Request (Rural) | Executing service disconnections and physical line removals upon request. | The distribution licensee must execute service disconnection and line shifting within 5 days for LT installations and within 7 days for HT installations in Rural Areas. | 99 | At least 99% of consumer-initiated disconnection requests must be processed within specified timelines. | N/A | No | N/A | Reported data not available.
Consumer Service Alterations | Line Phase or Voltage Conversion | Changing single-phase LT lines to three-phase LT lines (and vice-versa) or LT to HT. | The distribution licensee must complete line phase conversions or LT-to-HT conversions within 30 days from the date of payment of charges. | 99 | At least 99% of conversion works must be completed within 30 days. | N/A | No | N/A | Reported data not available.
Billing Complaints | Billing Disputes (No field report needed) | Correcting billing mistakes where no on-site investigation is required. | The distribution licensee must resolve complaints and issue a revised bill within 24 hours of receipt if no field report is required. | 99 | At least 99% of billing dispute complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
Billing Complaints | Billing Disputes (Field report required) | Correcting billing mistakes where on-site investigation is needed. | The distribution licensee must complete the field inspection and issue a revised bill within 7 days of receiving a billing dispute complaint. | 99 | At least 99% of billing dispute complaints must be resolved within the specified timeline. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Reconnection of Supply (Urban Areas) | Reconnecting supply following disconnection for non-payment upon dues settlement. | The distribution licensee must restore supply on the same day of receiving payment from the disconnected consumer in Cities and Towns. | 99 | At least 99% of urban reconnections must be completed on the same day. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Reconnection of Supply (Rural Areas) | Reconnecting supply following disconnection for non-payment upon dues settlement. | The distribution licensee must restore supply within 24 hours of receiving payment from the disconnected consumer in Rural Areas. | 99 | At least 99% of rural reconnections must be completed within 24 hours. | N/A | No | N/A | Reported data not available.
Administrative Remedies | Payment of Solatium (Accident Clear Cases) | Disbursing solatium compensation in cases of electrical accidents. | The distribution licensee must disburse solatium within 7 days (without waiting for the CEIG report) in clear cases where the accident is not due to the victim's fault. | 99 | At least 99% of solatium disbursements in clear cases must be executed within 7 days. | N/A | No | N/A | Reported data not available.
Administrative Remedies | Payment of Solatium (Other Accident Cases) | Disbursing solatium compensation in other electrical accident cases. | The distribution licensee must disburse solatium within 30 days after receiving the report from the CEIG in all other accident cases. | 95 | At least 95% of other solatium disbursements must be executed within 30 days of the CEIG report. | N/A | No | N/A | Reported data not available.
Administrative Remedies | Refund of Deposits | Returning security deposits or other deposits back to the consumer. | The distribution licensee must refund consumer deposits within 60 days of receiving a valid refund request. | 95 | At least 95% of deposit refunds must be executed within the 60-day limit. | N/A | No | N/A | Reported data not available.
Administrative Remedies | Issue of Certificates | Providing requested administrative or supply certificates to the consumer. | The distribution licensee must issue any requested certificates on the same day of receiving the consumer's request. | 99 | At least 99% of certificate issue requests must be completed on the same day. | N/A | No | N/A | Reported data not available.
Billing Efficiency | System Billing Performance | Ensuring proper coverage of consumer meters during each billing cycle. | The distribution licensee must bill 100% of metered active consumers within the designated billing cycle. | 100 | The utility must ensure 100% of the active consumer base is billed during each billing cycle. | N/A | No | N/A | Reported data not available.
Collection Efficiency | System Revenue Recovery (Metered) | Revenue collection benchmark against total billed energy for metered consumers. | The distribution licensee must achieve a minimum collection efficiency of 98% for metered installations. | 98 | The cumulative revenue recovery rate must meet or exceed the 98% target. | N/A | No | N/A | Reported data not available.
Collection Efficiency | System Revenue Recovery (Un-metered) | Revenue collection benchmark against total billed energy for un-metered consumers. | The distribution licensee must achieve a minimum collection efficiency of 85% for un-metered installations. | 85 | The cumulative revenue recovery rate must meet or exceed the 85% target. | N/A | No | N/A | Reported data not available.
System Operations | Distribution Transformer Failure Rate (Urban) | Restricting the annual failure rate of distribution transformers (DTR) in urban grids. | The distribution licensee must maintain the annual failure rate of distribution transformers at or below 3% in Urban Areas. | 3 | The overall annual transformer breakdown percentage must not exceed 3% in urban networks. | N/A | No | N/A | Reported data not available.
System Operations | Distribution Transformer Failure Rate (Rural) | Restricting the annual failure rate of distribution transformers (DTR) in rural grids. | The distribution licensee must maintain the annual failure rate of distribution transformers at or below 7% in Rural Areas. | 7 | The overall annual transformer breakdown percentage must not exceed 7% in rural networks. | N/A | No | N/A | Reported data not available.
System Operations | Active Meter Health (Faulty Meter Rate) | Managing the proportion of faulty/MNR/burnt/sticky meters in the network. | The distribution licensee must limit the percentage of faulty meters in service (including MNR, burnt, sticky, and faulty units) to not exceed 1.5%. | 1.5 | The overall percentage of faulty active meters in service must be kept below the 1.5% ceiling. | N/A | No | N/A | Reported data not available.
System Operations | Voltage Regulation at Supply Point (LT) | Maintaining phase voltage within regulatory limits at the point of commencement of supply. | The distribution licensee must maintain the terminal supply voltage on the LT system within the limits of +6% and -6%. | 100 | The terminal voltage across all LT consumers must fully comply with the ±6% variation boundaries. | N/A | No | N/A | Reported data not available.
System Operations | Voltage Regulation at Supply Point (HT) | Maintaining phase voltage within regulatory limits at the point of commencement of supply. | The distribution licensee must maintain the terminal supply voltage on the HT system within the limits of +6% and -9%. | 100 | The terminal voltage across all HT consumers must fully comply with the +6% and -9% variation boundaries. | N/A | No | N/A | Reported data not available.
System Operations | Voltage Regulation at Supply Point (EHT) | Maintaining phase voltage within regulatory limits at the point of commencement of supply. | The distribution licensee must maintain the terminal supply voltage on the EHT system within the limits of +12.5% and -12.5%. | 100 | The terminal voltage across all EHT consumers must fully comply with the ±12.5% variation boundaries. | N/A | No | N/A | Reported data not available.

## ANDHRA PRADESH
Andhra Pradesh Electricity Regulatory Commission (Licensees’ Standards of Performance) Regulation, 2004 | APERC (Licensees' Standards of Performance Second Amendment) Regulation, 2013 | APERC (Licensees' Standards of Performance) Fourth Amendment Regulation, 2023 | Fifth Amendment to Andhra Pradesh Electricity Regulatory Commission (Licensees' Standards of Performance) Regulation, 2024 | Sixth Amendment to Andhra Pradesh Electricity Regulatory Commission (Licensees' Standards of Performance) Regulation, 2025
Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data | Comparison Possible? | Standard met? | If comparison not possible, why?
Restoration of Power Supply | Normal Fuse-off Calls (Cities & Towns) | Replacing Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or at consumer premises. | The distribution licensee must replace blown fuses and restore supply following normal fuse-off calls within 4 working hours of receiving a complaint in cities and towns. | 99 | At least 99% of total fuse-off calls received must be rectified within specified limits. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Normal Fuse-off Calls (Rural Areas) | Replacing Horn Gap (HG) or Low Tension (LT) fuses at distribution transformers or consumer premises. | The distribution licensee must replace blown fuses and restore supply following normal fuse-off calls within 12 working hours of receiving a complaint in rural areas. | 99 | At least 95% of line breakdown cases must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Overhead Line/Cable Breakdowns (Cities & Towns) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | The distribution licensee must resolve overhead line or cable breakdowns and restore supply within 6 hours of occurrence in cities and towns. | 95 | At least 95% of line breakdown cases must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Overhead Line/Cable Breakdowns (Rural Areas) | Repairing overhead distribution lines or cables, excluding cases with broken or uprooted poles. | The distribution licensee must resolve overhead line or cable breakdowns and restore supply within 24 hours of occurrence in rural areas. | 95 | At least 95% of line breakdown cases must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Underground Cable Breakdowns (Cities & Towns) | Locating, repairing, and re-energising the system following underground cable network faults. | The distribution licensee must resolve underground cable faults and restore supply within 12 hours of occurrence in cities and towns. | 95 | At least 95% of line breakdown cases must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Underground Cable Breakdowns (Rural Areas) | Locating, repairing, and re-energising the system following underground cable network faults. | The distribution licensee must resolve underground cable faults and restore supply within 48 hours of occurrence in rural areas. | 95 | At least 95% of failed distribution transformers must be replaced within specified limits. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Distribution Transformer Failure (Cities & Towns) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | The distribution licensee must replace or repair a failed distribution transformer and restore supply within 24 hours of receiving the complaint in cities and towns. | 95 | At least 95% of failed distribution transformers must be replaced within specified limits. | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Distribution Transformer Failure (Rural Areas) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | The distribution licensee must replace or repair a failed distribution transformer and restore supply within 48 working hours of receiving the complaint in rural areas. | 95 | At least 95% of scheduled outages must comply with the maximum daily duration standard. | N/A | No | N/A | Reported data not available.
System Outages | Scheduled Outages (Duration) | Pre-arranged shut-downs of equipment and lines for necessary maintenance work. | The distribution licensee must limit the maximum duration of a scheduled outage for system maintenance to not exceed 12 hours in a day. | 95 | At least 95% of scheduled outages must have supply restored by 6:00 PM. | N/A | No | N/A | Reported data not available.
System Outages | Scheduled Outages (Restoration) | Pre-arranged shut-downs of equipment and lines for necessary maintenance work. | During pre-arranged maintenance outages, the distribution licensee must ensure that the power supply is fully restored by not later than 6:00 PM. | 95 | At least 90% of street light line faults must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
Street Light Complaints | Street Light Faults (Line Faults) | Rectifying overhead line faults and restoring streetlights. | The distribution licensee must rectify line faults and restore streetlights within 24 hours of detection or receipt of a complaint, whichever is earlier. | 90 | At least 90% of defective street light fixtures must be replaced within specified limits. | N/A | No | N/A | Reported data not available.
Street Light Complaints | Defective Street Light Fixtures | Replacing fused bulbs or rectifying/replacing defective street lighting units. | The distribution licensee must replace the light or rectify/replace the unit within 24 hours of detection or receipt of a complaint, whichever is earlier, wherever responsible for maintenance. | 90 | The overall billing error rate requiring modifications must remain under the 0.1% ceiling. | N/A | No | N/A | Reported data not available.
Billing Complaints | Billing Mistakes (System Error Rate) | Managing the error rate of issued bills requiring modifications. | The distribution licensee must limit the percentage of bills requiring modifications following complaints to the total number of bills issued to not exceed 0.1. | 0.1 | At least 99% of billing complaints must be resolved within specified timelines. | N/A | No | N/A | Reported data not available.
Billing Complaints | Billing Disputes (No inspection) | Correcting billing errors where no additional on-site inspection or information is required. | When a billing complaint is received and no additional information is required, the licensee must resolve the dispute and issue a revised bill within 24 working hours of receipt of the complaint. | 99 | At least 99% of billing complaints must be resolved within specified timelines. | N/A | No | N/A | Reported data not available.
Billing Complaints | Billing Disputes (With inspection) | Correcting billing errors where additional on-site inspection or meter verification is required. | When a billing complaint is received and additional information or investigation is required, the licensee must resolve the dispute and issue a revised bill within 7 working days. | 99 | The overall percentage of active faulty meters across the network must not exceed the 3% cap. | N/A | No | N/A | Reported data not available.
Metering Complaints | System Meter Health | Maintaining overall meter health across the distribution network. | The distribution licensee must maintain the percentage of defective meters in service at a value not greater than 3 of the total number of meters in service. | 3 | At least 99% of meter complaints in cities and towns must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
Metering Complaints | Meter Correctness (Cities & Towns) | Inspecting, checking correctness, and replacing reported malfunctioning meters in urban areas. | The distribution licensee must inspect and check the correctness of a meter within 7 working days of complaint and, if found not working, replace it within 15 days thereafter in cities and towns. | 99 | At least 98% of meter complaints in rural areas must be resolved within specified limits. | N/A | No | N/A | Reported data not available.
Metering Complaints | Meter Correctness (Rural Areas) | Inspecting, checking correctness, and replacing reported malfunctioning meters in rural areas. | The distribution licensee must inspect and check the correctness of a meter within 15 working days of complaint and, if found not working, replace it within 15 days thereafter in rural areas. | 98 | At least 99% of urban and 98% of rural burnt meter complaints must be resolved within specified standards. | N/A | No | N/A | Reported data not available.
Metering Complaints | Burnt Meter (Licensee Cause) | Replacing burnt-out meters due to network failures (such as high voltage, loose contacts, or age). | The distribution licensee must replace a burnt-out meter at its own cost within 24 hours in urban areas and 72 hours in rural areas from receipt of complaint, if the burning is due to licensee-attributable causes. | 99 : Urrban 98 : Rural | At least 99% of urban and 98% of rural burnt meter complaints must be resolved within specified standards. | N/A | No | N/A | Reported data not available.
Metering Complaints | Burnt Meter (Consumer Cause) | Replacing burnt-out meters due to consumer overloading, tampering, or wet meters. | The distribution licensee must replace a burnt-out meter within 24 hours in urban areas and 72 hours in rural areas of receiving the payment of meter cost from the consumer, if the burning is due to consumer causes. | 99 : Urrban 98 : Rural | At least 98% of voltage unbalance issues must be successfully maintained within the specified threshold. | N/A | No | N/A | Reported data not available.
Voltage Issues | Voltage Unbalance | Maintaining supply voltage phase symmetry at the point of supply. | The distribution licensee must ensure that the phase voltage unbalance does not exceed 3 at the point of commencement of supply. | 98 | At least 98% of voltage fluctuation cases must be rectified within specified timelines. | N/A | No | N/A | Reported data not available.
Voltage Issues | Voltage Fluctuations (No network expansion) | Resolving voltage level issues where distribution mains do not require expansion. | The distribution licensee must resolve voltage level complaints and bring voltages within prescribed limits (±6 for LT, +6/-9 for HT, +10/-12.5 for EHT) within 10 days of the complaint. | 98 | At least 98% of voltage fluctuation cases must be rectified within specified timelines. | N/A | No | N/A | Reported data not available.
Voltage Issues | Voltage Fluctuations (System Upgrade) | Resolving voltage level issues where system network upgrade is required. | Where resolving voltage fluctuations requires system up-gradation or network enhancement, the distribution licensee must complete the works within 120 days. | 98 | At least 98% of voltage fluctuation cases must be rectified within specified timelines. | N/A | No | N/A | Reported data not available.
Voltage Issues | Voltage Fluctuations (Substation Erection) | Resolving voltage level issues when a new substation needs to be erected. | When resolving a voltage issue requires erecting a new substation, the utility must complete the installation and commission it within the timeframe approved by the Commission. | 98 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | Feasible Connection (Existing network) | Releasing supply where distribution mains are already in place. | The distribution licensee must release a new electricity connection within 30 days of receiving a complete application accompanied by prescribed fees, charges, and security. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | High Tension (HT) Connection - 11 KV | Releasing 11 KV supply when network extension is required. | The distribution licensee must complete the network extension and release supply within 60 days of receipt of prescribed charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | High Tension (HT) Connection - 33 KV | Releasing 33 KV supply when network extension is required. | The distribution licensee must complete the network extension and release supply within 90 days of receipt of prescribed charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | Extra High Tension (EHT) Connection | Releasing EHT supply when transmission network extension is required. | The distribution licensee must complete the extra high tension network extension and release supply within 180 days of receipt of prescribed charges. | 100 | All cases (100%) of release of connection must be completed within the specified limits. | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | Substation Erection | Releasing supply when a new substation must be erected. | Where supply requires the commissioning of a new substation, the distribution licensee must supply electricity immediately after commissioning within a period not exceeding 90 days. | 100 | At least 98% of administrative service requests must be completed within specified limits. | N/A | No | N/A | Reported data not available.
Consumer Service Alterations | Title Transfer of Ownership | Processing the transfer of ownership of a service connection to a new owner. | The distribution licensee must process and finalize the transfer of ownership of a connection within 7 days of receiving the application with necessary documents and fee. | 98 | At least 98% of administrative service requests must be completed within specified limits. | N/A | No | N/A | Reported data not available.
Consumer Service Alterations | Change of Category | Processing the change of consumer or tariff category. | The distribution licensee must process and finalize the request for change of category within 7 days of receiving the application with necessary documents and fee. | 98 | At least 98% of technical service requests must be completed within specified limits. | N/A | No | N/A | Reported data not available.
Consumer Service Alterations | LT Phase Conversion | Converting service lines from LT single-phase to LT three-phase (or vice-versa). | The distribution licensee must execute and complete phase conversion from LT single-phase to LT three-phase (or vice-versa) within 30 days of payment of necessary charges. | 98 | At least 98% of technical service requests must be completed within specified limits. | N/A | No | N/A | Reported data not available.
Consumer Service Alterations | LT to HT Conversion | Converting service connections from Low Tension to High Tension (or vice-versa). | The distribution licensee must execute and complete service conversion from Low Tension to High Tension (or vice-versa) within 60 days of payment of necessary charges. | 98 | At least 98 of technical service requests must be completed within specified limits. | N/A | No | N/A | Reported data not available.

## WEST BENGAL
West Bengal Electricity Regulatory Commission (Standards of Performance of Licensees Relating to Consumer Services) Regulations, 2010 | West Bengal Electricity Regulatory Commission (Standards of Performance of Licensees Relating to Consumer Services) (First Amendment) Regulations, 2013.
Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data | Comparison Possible? | Standard met? | If comparison not possible, why?
Restoration of Power Supply | Failure of licensee's fuse (Urban) | Restoring power supply by replacing blown fuses at distribution transformers or consumer premises. | The distribution licensee must replace blown fuses and restore supply within 3 hours in urban areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Failure of licensee's fuse (Rural - Monsoon) | Restoring power supply by replacing blown fuses at distribution transformers or consumer premises during monsoon. | The distribution licensee must replace blown fuses and restore supply within 8 hours during the Monsoon season (June to September) in rural areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Failure of licensee's fuse (Rural - Non-Monsoon) | Restoring power supply by replacing blown fuses at distribution transformers or consumer premises during non-monsoon. | The distribution licensee must replace blown fuses and restore supply within 6 hours during non-monsoon months (October to May) in rural areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Snapping of LT wires (Urban) | Repairing broken or snapped Low Tension (LT) overhead wires. | The distribution licensee must repair snapped LT wires and restore supply within 4 hours in urban areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Snapping of LT wires (Rural - Monsoon) | Repairing broken or snapped Low Tension (LT) overhead wires during monsoon. | The distribution licensee must repair snapped LT wires and restore supply within 16 hours during the Monsoon season (June to September) in rural areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Snapping of LT wires (Rural - Non-Monsoon) | Repairing broken or snapped Low Tension (LT) overhead wires during non-monsoon. | The distribution licensee must repair snapped LT wires and restore supply within 10 hours during non-monsoon months (October to May) in rural areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Falling of trees on overhead lines (Urban) | Clearing fallen trees or branches from LT and HT overhead lines without broken/uprooted poles. | The distribution licensee must clear fallen trees and restore supply within 8 hours in urban areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Falling of trees on overhead lines (Rural) | Clearing fallen trees or branches from LT and HT overhead lines without broken/uprooted poles. | The distribution licensee must clear fallen trees and restore supply within 24 hours in rural areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | LT underground cable short circuit (Urban) | Repairing short circuits on underground LT cable networks. | The distribution licensee must repair LT underground cable short circuits and restore supply within 6 hours in urban areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | LT overhead line short circuit (Urban) | Repairing short circuits on overhead LT line networks. | The distribution licensee must repair LT overhead line short circuits and restore supply within 3 hours in urban areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | LT overhead line short circuit (Rural) | Repairing short circuits on overhead LT line networks. | The distribution licensee must repair LT overhead line short circuits and restore supply within 4 hours in rural areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | 11 KV overhead line breakdown (Urban - No pole) | Resolving 11 KV overhead breakdowns where no poles are broken or need replacement. | The distribution licensee must restore supply within 6 hours of an 11 KV line breakdown in urban areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | 11 KV overhead line breakdown (Rural - No pole) | Resolving 11 KV overhead breakdowns where no poles are broken or need replacement. | The distribution licensee must restore supply within 18 hours of an 11 KV line breakdown in rural areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | 11 KV overhead line breakdown (Urban - Pole replacement) | Resolving breakdowns where poles are broken/uprooted and need replacement. | The distribution licensee must replace broken poles and restore supply within 12 hours in urban areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | 11 KV overhead line breakdown (Rural - Pole replacement) | Resolving breakdowns where poles are broken/uprooted and need replacement. | The distribution licensee must replace broken poles and restore supply within 24 hours in rural areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | HT underground cable fault (Ring Main) | Repairing HT underground cable failures where a ring main supply system exists. | The distribution licensee must restore power supply within 4 hours using alternative ring main feeds. | N/A | N/A | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | HT underground cable fault (No Ring Main) | Repairing HT underground cable failures where no ring main system exists. | The distribution licensee must isolate, repair, and restore supply within 24 hours where no ring main feed exists. | N/A | N/A | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Distribution Transformer Failure (Urban) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | The distribution licensee must replace or repair a failed distribution transformer and restore supply within 12 hours in urban areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Distribution Transformer Failure (Rural) | Replacing or repairing failed distribution transformers and restoring consumer service lines. | The distribution licensee must replace or repair a failed distribution transformer and restore supply within 48 hours in rural areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | LT line breakdowns for other reasons (Urban) | Resolving any other general LT line failures not categorized elsewhere. | The distribution licensee must resolve LT line failures and restore supply within 6 hours in urban areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | LT line breakdowns for other reasons (Rural) | Resolving any other general LT line failures not categorized elsewhere. | The distribution licensee must resolve LT line failures and restore supply within 24 hours in rural areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Service Line Failure (Urban - OH / UG) | Restoring service lines directly feeding consumer premises. | The distribution licensee must resolve service line failures within 4 hours (Overhead) or 12 hours (Underground) in urban areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Restoration of Power Supply | Service Line Failure (Rural - OH / UG) | Restoring service lines directly feeding consumer premises. | The distribution licensee must resolve service line failures within 18 hours (Overhead) or 24 hours (Underground) in rural areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Voltage Issues | Under / Over Voltage (Local Problem) | Correcting local voltage level anomalies. | The distribution licensee must resolve persistent local over/under voltage complaints within 15 days. | N/A | N/A | N/A | No | N/A | Reported data not available.
Voltage Issues | Under / Over Voltage (System Augmentation) | Correcting voltage level anomalies that require network restructuring. | Where voltage corrections require distribution system augmentation or line re-routing, the licensee must complete works within 6 months. | N/A | N/A | N/A | No | N/A | Reported data not available.
Voltage Issues | Voltage Fluctuations (Urban) | Attending to complaints regarding voltage fluctuation beyond State Grid Code limits. | The distribution licensee must resolve voltage fluctuation complaints within 4 days in urban areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Voltage Issues | Voltage Fluctuations (Rural) | Attending to complaints regarding voltage fluctuation beyond State Grid Code limits. | The distribution licensee must resolve voltage fluctuation complaints within 8 days in rural areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Metering Complaints | Defective Meter Inspection (Urban - No supply cut-off) | Inspecting malfunctioning, creeping, or stuck meters (Amended in 2013). | The distribution licensee must inspect defective meters within 3 working days of receiving a complaint in urban areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Metering Complaints | Defective Meter Inspection (Rural - No supply cut-off) | Inspecting malfunctioning, creeping, or stuck meters (Amended in 2013). | The distribution licensee must inspect defective meters within 7 working days of receiving a complaint in rural areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Metering Complaints | Burnt Meter Replacement (Urban - No supply cut-off) | Replacing burnt meters where supply remains live (Amended in 2013). | The distribution licensee must replace a burnt meter within 7 working days of inspection in urban areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Metering Complaints | Burnt Meter Replacement (Rural - No supply cut-off) | Replacing burnt meters where supply remains live (Amended in 2013). | The distribution licensee must replace a burnt meter within 15 working days of inspection in rural areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Metering Complaints | Defective Meter Replacement (Urban & Rural) | Replacing or rectifying malfunctioning meters (Amended in 2013). | The distribution licensee must test and replace defection meters within 20 days of inspection in both urban and rural areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Metering Complaints | Faulty Meter Replacement (Urban - Supply affected) | Replacing faulty/burnt meters where supply is interrupted. | The distribution licensee must replace a faulty meter and restore supply within 24 hours of complaint in urban areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Metering Complaints | Faulty Meter Replacement (Rural - Supply affected) | Replacing faulty/burnt meters where supply is interrupted. | The distribution licensee must replace a faulty meter and restore supply within 48 hours of complaint in rural areas. | N/A | N/A | N/A | No | N/A | Reported data not available.
Metering Complaints | Breakage of Seals (Sealing only) | Resealing accidental breakage of seals where no tampering is suspected. | The distribution licensee must reseal meters within 24 hours of complaint or detection. | N/A | N/A | N/A | No | N/A | Reported data not available.
Metering Complaints | Breakage of Seals (Replacement) | Replacing meters following seal breakage where replacement is required (Amended in 2013). | The distribution licensee must replace meters with broken seals within 10 days of complaint or detection. | N/A | N/A | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | Quotation Issue (Urban - LV & MV) | Conducting inspection and issuing estimates/quotations for new LV/MV connections. | The distribution licensee must inspect premises and issue connection quotations within 14 days of receiving request. | N/A | N/A | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | Quotation Issue (Rural - LV & MV) | Conducting inspection and issuing estimates/quotations for new LV/MV connections. | The distribution licensee must inspect premises and issue connection quotations within 28 days of receiving request. | N/A | N/A | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | Quotation Issue (HT - 11 KV / 33 KV / 132 KV) | Conducting inspection and issuing estimates/quotations for HT supply. | The distribution licensee must inspect and issue estimates within 30 days (11 KV), 45 days (33 KV), or 60 days (132 KV) of request. | N/A | N/A | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | New Connection (Existing Network) | Releasing new LT/MV connections where distribution mains exist. | The distribution licensee must release a new electricity connection within 30 days of receiving a completed application (Form B). | N/A | N/A | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | Network Augmentation (LV/MV - No poles) | Releasing connections requiring distribution main augmentation but no additional poles (Amended in 2013). | The distribution licensee must release the new connection within 60 days of application (Form B). | N/A | N/A | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | Network Augmentation (LV/MV - UG Cable < 100m) | Releasing connections requiring cable extension up to 100 metres (Amended in 2013). | The distribution licensee must release the new connection within 60 days of application (Form B). | N/A | N/A | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | Network Augmentation (LV/MV - Additional poles) | Releasing connections requiring overhead line extension with additional poles (Amended in 2013). | The distribution licensee must release the new connection within 90 days of application (Form B). | N/A | N/A | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | Network Augmentation (LV/MV - UG Cable > 100m) | Releasing connections requiring underground cable extension above 100 metres. | The distribution licensee must release the new connection within 90 days of application (Form B). | N/A | N/A | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | Network Augmentation (HV & EHV) | Releasing HV or EHV supply when network extension is required. | The distribution licensee must release new HV/EHV connections within 180 days of application (Form B). | N/A | N/A | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | Existing Substation Bay / Transformer Commissioning | Installing new transformers or bays in existing substations. | The licensee must complete installation within 90 days (Distribution Substation), 150 days (33 KV Substation), or 270 days (132 KV Substation) of application. | N/A | N/A | N/A | No | N/A | Reported data not available.
New Connections / Load Changes | New Substation Erection | Erecting and commissioning new substations to release connection. | The licensee must complete erection within 90 days (Distribution Substation), 300 days (33/11 KV Substation), or 540 days (132/33 KV Substation) of taking possession of land or ROW. | N/A | N/A | N/A | No | N/A | Reported data not available.
Extension of Load for Existing Consumers | Load Extension (Existing network - OH) | Increasing sanctioned load where existing lines can accommodate it. | The distribution licensee must execute load extension within 30 days of application for consumers having overhead lines. | N/A | N/A | N/A | No | N/A | Reported data not available.
Extension of Load for Existing Consumers | Load Extension (Existing network - UG) | Increasing sanctioned load where cable augmentation is required. | The distribution licensee must execute load extension within 45 days of application for consumers on underground cables. | N/A | N/A | N/A | No | N/A | Reported data not available.
Extension of Load for Existing Consumers | Load Extension (Network expansion - LV & MV) | Increasing sanctioned load requiring overhead line extension with no additional poles, additional poles, or UG cables. | The licensee must execute load extension within 45 days (No expansion), 60 days (OH - No poles), or 90 days (OH - Additional poles / UG cables) of application. | N/A | N/A | N/A | No | N/A | Reported data not available.
Extension of Load for Existing Consumers | Load Extension (Existing Substation works) | Increasing load requiring substation transformer or bay commissioning. | The licensee must complete substation works within 90 days (Distribution Substation), 150 days (33 KV Substation), or 270 days (132 KV Substation). | N/A | N/A | N/A | No | N/A | Reported data not available.
Consumer Service Alterations | Alteration of Service (Meter / board within premises) | Processing requests to shift or alter meters/service lines within consumer boundaries. | The distribution licensee must complete physical alterations within 30 days of application. | N/A | N/A | N/A | No | N/A | Reported data not available.
Consumer Service Alterations | Alteration of Service (Other alterations) | Shifting service lines or distribution equipment outside consumer boundaries. | The distribution licensee must complete alterations within 90 days of application. | N/A | N/A | N/A | No | N/A | Reported data not available.
Consumer Service Alterations | Name Transfer / Purpose Conversion / Load Reduction | Transferring connection ownership, category conversion, or contract demand reduction (single application in Form A1). | The distribution licensee must complete transfer or conversion within the next billing cycle without discontinuing supply. | N/A | N/A | N/A | No | N/A | Reported data not available.
Consumer Service Alterations | Voluntary Disconnection of Supply | Processing requests for permanent service disconnection. | The distribution licensee must effect voluntary disconnection immediately within the notice period specified in the Supply Code. | N/A | N/A | N/A | No | N/A | Reported data not available.
System Outages | Planned Interruption Notification | Restricting duration and ensuring prior notice of scheduled maintenance outages. | For pre-planned interruptions lasting more than 6 hours, the licensee must notify affected consumers at least 3 days in advance. | Advance Notice | Required via announcements, newspaper ads, radio/TV, or loudspeaker. | N/A | No | N/A | Reported data not available.

## DGVCL,GUJARAT
Dakshin Gujarat Vij Company Limited
Gujarat Electricity Regulatory Commission (Standards of Performance of Distribution Licensees) Regulations, 2023. | Gujarat Electricity Regulatory Commission (Standard of Performance of Distribution Licensee) Regulations, 2005 | 2005 Regulations apply up to 5 Dec 2023 and the 2023 Regulations apply from 6 Dec 2023. FY 2023-24 must therefore be treated as a split-regulation year.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Quality of Supply | Neutral Voltage | The presence of electrical potential on the neutral conductor relative to earth, indicating an imbalance or faulty grounding. | If rectification is not feasible immediately, inform the consumer of the likely completion timeline within 3 days in Urban areas and 7 days in Rural areas. | 2 | Keep neutral voltage from exceeding 2% of the supply voltage. | 0 | No. of deviation of results from the sample test
2021-22 | Cosumer complaints | Classification of Complaints | Organizing consumer complaints into specific technical, billing, or service categories. | N/A | N/A | N/A | 100 | % of registered complaints redressed in standard time | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Faulty meter | Meter reported by a consumer or detected by the utility as defective, stopped, burnt, stolen, or improperly recording. | Inspect, check, or test the meter within 7 working days in Urban areas and within 15 working days in Rural areas of receiving a complaint. If found defective, replace the meter and restore the electricity supply within 24 hours in Urban areas and within 72 hours in Rural areas from the time of inspection or testing. | N/A | N/A | Single-Phase: 21,894 and Three-Phase: 12,555 (total 34,449) | No. of faulty meters pending at year-end | No | N/A | No benchmark defined in regulations.
2021-22 | New connections | Release of new connections | Releasing and energising a new electricity connection upon receiving the applicant's full payment of the demand note and necessary test report. | For general-purpose connections, the 2005 Regulations require the demand note within 7 days and connection within 20 days after payment/formalities; where mains/substation extension is needed, the outer period is 2 months Urban / 4 months Rural. | N/A | N/A | 83.85% | % of connections released out of the total applications | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Quality of Supply | Neutral Voltage | The presence of electrical potential on the neutral conductor relative to earth, indicating an imbalance or faulty grounding. | If rectification is not feasible immediately, inform the consumer of the likely completion timeline within 3 days in Urban areas and 7 days in Rural areas. | 2 | Keep neutral voltage from exceeding 2% of the supply voltage. | 0 | No. of deviation of results from the sample test
2022-23 | Cosumer complaints | Classification of Complaints | Organizing consumer complaints into specific technical, billing, or service categories. | N/A | N/A | N/A | 100 | % of registered complaints redressed in standard time | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Faulty meter | Meter reported by a consumer or detected by the utility as defective, stopped, burnt, stolen, or improperly recording. | For the period up to 5 Dec 2023, the 2005 rules apply: inspect/test within 7 working days Urban / 15 working days Rural; a defective meter is generally to be replaced within 15 days after inspection/testing. From 6 Dec 2023, If found defective, replace the meter and restore the electricity supply within 24 hours in Urban areas and within 72 hours in Rural areas from the time of inspection or testing. | N/A | N/A | Single-Phase: 46,607 and Three-Phase: 16,832 (total 63,439) | No. of faulty meters pending at year-end | No | N/A | No benchmark defined in regulations.
2022-23 | New connections | Release of new connections | Releasing and energising a new electricity connection upon receiving the applicant's full payment of the demand note and necessary test report. | For general-purpose connections, the 2005 Regulations require the demand note within 7 days and connection within 20 days after payment/formalities; where mains/substation extension is needed, the outer period is 2 months Urban / 4 months Rural. | N/A | N/A | 92.08 | % of connections released out of the total applications | No | N/A | Data not reported
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Quality of Supply | Neutral Voltage | The presence of electrical potential on the neutral conductor relative to earth, indicating an imbalance or faulty grounding. | If rectification is not feasible immediately, inform the consumer of the likely completion timeline within 3 days in Urban areas and 7 days in Rural areas. | 2 | Keep neutral voltage from exceeding 2% of the supply voltage. | 0 | No. of deviation of results from the sample test
2023-24 | Cosumer complaints | Classification of Complaints | Organizing consumer complaints into specific technical, billing, or service categories. | N/A | N/A | N/A | 100 | % of registered complaints redressed in standard time | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Faulty meter | Meter reported by a consumer or detected by the utility as defective, stopped, burnt, stolen, or improperly recording. | For the period up to 5 Dec 2023, the 2005 rules apply: inspect/test within 7 working days Urban / 15 working days Rural; a defective meter is generally to be replaced within 15 days after inspection/testing. From 6 Dec 2023, If found defective, replace the meter and restore the electricity supply within 24 hours in Urban areas and within 72 hours in Rural areas from the time of inspection or testing. | N/A | N/A | Total : 147,635; Single-Phase : 111,267; Three-Phase: 36,368 | No. of faulty meters pending at year-end | No | N/A | No benchmark defined in regulations.
2023-24 | New connections | Release of new connections | Releasing and energising a new electricity connection upon receiving the applicant's full payment of the demand note and necessary test report. | For general-purpose connections, the 2005 Regulations require the demand note within 7 days and connection within 20 days after payment/formalities; where mains/substation extension is needed, the outer period is 2 months Urban / 4 months Rural. | N/A | N/A | 96.85 | % of connections released out of the total applications | No | N/A | Data not reported
2024-25 | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Quality of Supply | Neutral Voltage | The presence of electrical potential on the neutral conductor relative to earth, indicating an imbalance or faulty grounding. | If rectification is not feasible immediately, inform the consumer of the likely completion timeline within 3 days in Urban areas and 7 days in Rural areas. | 2 | Keep neutral voltage from exceeding 2% of the supply voltage. | 0 | No. of deviation of results from the sample test
2024-25 | Cosumer complaints | Classification of Complaints | Organizing consumer complaints into specific technical, billing, or service categories. | N/A | N/A | N/A | N/A | N/A | No | N/A | Data not reported
2024-25 | Restoration of Supply | Faulty meter | Meter reported by a consumer or detected by the utility as defective, stopped, burnt, stolen, or improperly recording. | Inspect, check, or test the meter within 7 working days in Urban areas and within 15 working days in Rural areas of receiving a complaint. If found defective, replace the meter and restore the electricity supply within 24 hours in Urban areas and within 72 hours in Rural areas from the time of inspection or testing. | N/A | N/A | N/A | No. of faulty meters pending at year-end | No | N/A | No benchmark defined in regulations.
2024-25 | New connections | Release of new connections | Releasing and energising a new electricity connection upon receiving the applicant's full payment of the demand note and necessary test report. | Energise and release the connection within: 7 days in Urban areas and 10 days in Rural areas if provided from the existing distribution network; 15 days if network modification requires extending the LT line up to 150 metres; 21 days if network modification requires extending the LT line more than 150 metres and/or augmenting the distribution transformer; 30 days if network modification requires erecting a new distribution transformer; 90 days if network modification requires erecting a new HT line and distribution transformer and/or augmenting the existing HT line network; 180 days if network modification requires erecting/augmenting an EHT level line and/or substation. | N/A | N/A | N/A | % of connections released out of the total applications | No | N/A | Data not reported
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Quality of Supply | Neutral Voltage | The presence of electrical potential on the neutral conductor relative to earth, indicating an imbalance or faulty grounding. | If rectification is not feasible immediately, inform the consumer of the likely completion timeline within 3 days in Urban areas and 7 days in Rural areas. | 2 | Keep neutral voltage from exceeding 2% of the supply voltage. | 0 | No. of deviation of results from the sample test
2025-26 | Cosumer complaints | Classification of Complaints | Organizing consumer complaints into specific technical, billing, or service categories. | N/A | N/A | N/A | N/A | N/A | No | N/A | Data not reported
2025-26 | Restoration of Supply | Faulty meter | Meter reported by a consumer or detected by the utility as defective, stopped, burnt, stolen, or improperly recording. | Inspect, check, or test the meter within 7 working days in Urban areas and within 15 working days in Rural areas of receiving a complaint. If found defective, replace the meter and restore the electricity supply within 24 hours in Urban areas and within 72 hours in Rural areas from the time of inspection or testing. | N/A | N/A | N/A | No. of faulty meters pending at year-end | No | N/A | No benchmark defined in regulations.
2025-26 | New connections | Release of new connections | Releasing and energising a new electricity connection upon receiving the applicant's full payment of the demand note and necessary test report. | Energise and release the connection within: 7 days in Urban areas and 10 days in Rural areas if provided from the existing distribution network; 15 days if network modification requires extending the LT line up to 150 metres; 21 days if network modification requires extending the LT line more than 150 metres and/or augmenting the distribution transformer; 30 days if network modification requires erecting a new distribution transformer; 90 days if network modification requires erecting a new HT line and distribution transformer and/or augmenting the existing HT line network; 180 days if network modification requires erecting/augmenting an EHT level line and/or substation. | N/A | N/A | N/A | % of connections released out of the total applications | No | N/A | Data not reported

## MGVCL,GUJARAT
Madhya Gujarat Vij Company Limited
Gujarat Electricity Regulatory Commission (Standards of Performance of Distribution Licensees) Regulations, 2023. | Gujarat Electricity Regulatory Commission (Standard of Performance of Distribution Licensee) Regulations, 2005 | 2005 Regulations apply up to 5 Dec 2023 and the 2023 Regulations apply from 6 Dec 2023.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Quality of Supply | Neutral Voltage | The presence of electrical potential on the neutral conductor relative to earth, indicating an imbalance or faulty grounding. | If rectification is not feasible immediately, inform the consumer of the likely completion timeline within 3 days in Urban areas and 7 days in Rural areas. | 2 | Keep neutral voltage from exceeding 2% of the supply voltage. | 0 | No. of deviation of results from the sample test
2021-22 | Cosumer complaints | Classification of Complaints | Organizing consumer complaints into specific technical, billing, or service categories. | N/A | N/A | N/A | 100 | % of registered complaints redressed in standard time | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Faulty meter | Meter reported by a consumer or detected by the utility as defective, stopped, burnt, stolen, or improperly recording. | inspect/test within 7 working days Urban / 15 working days Rural; a defective meter is generally replaced within 15 days after inspection/testing. | N/A | N/A | Single phase: 9,127 / Three phase: 1,947 | No. of faulty meters pending at year-end | No | N/A | No benchmark defined in regulations.
2021-22 | New connections | Release of new connections | Releasing and energising a new electricity connection upon receiving the applicant's full payment of the demand note and necessary test report. | General-purpose demand note within 7 days and connection within 20 days after payment/formalities where the distribution system exists; where mains/substation extension is needed, the outer period is 2 months Urban / 4 months Rural | N/A | N/A | 76.49 | % of connections released out of the total applications | No | N/A | Data not reported
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Quality of Supply | Neutral Voltage | The presence of electrical potential on the neutral conductor relative to earth, indicating an imbalance or faulty grounding. | If rectification is not feasible immediately, inform the consumer of the likely completion timeline within 3 days in Urban areas and 7 days in Rural areas. | 2 | Keep neutral voltage from exceeding 2% of the supply voltage. | 0 | No. of deviation of results from the sample test
2022-23 | Cosumer complaints | Classification of Complaints | Organizing consumer complaints into specific technical, billing, or service categories. | N/A | N/A | N/A | 100 | % of registered complaints redressed in standard time | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Faulty meter | Meter reported by a consumer or detected by the utility as defective, stopped, burnt, stolen, or improperly recording. | inspect/test within 7 working days Urban / 15 working days Rural; a defective meter is generally replaced within 15 days after inspection/testing. | N/A | N/A | Single phase: 6,657 /Three phase: 711 | No. of faulty meters pending at year-end | No | N/A | No benchmark defined in regulations.
2022-23 | New connections | Release of new connections | Releasing and energising a new electricity connection upon receiving the applicant's full payment of the demand note and necessary test report. | General-purpose demand note within 7 days and connection within 20 days after payment/formalities where the distribution system exists; where mains/substation extension is needed, the outer period is 2 months Urban / 4 months Rural | N/A | N/A | 73.47 | % of connections released out of the total applications | No | N/A | Data not reported
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Quality of Supply | Neutral Voltage | The presence of electrical potential on the neutral conductor relative to earth, indicating an imbalance or faulty grounding. | If rectification is not feasible immediately, inform the consumer of the likely completion timeline within 3 days in Urban areas and 7 days in Rural areas. | 2 | Keep neutral voltage from exceeding 2% of the supply voltage. | 0 | No. of deviation of results from the sample test
2023-24 | Cosumer complaints | Classification of Complaints | Organizing consumer complaints into specific technical, billing, or service categories. | N/A | N/A | N/A | 100 | % of registered complaints redressed in standard time | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Faulty meter | Meter reported by a consumer or detected by the utility as defective, stopped, burnt, stolen, or improperly recording. | Before 6 Dec 2023, the 2005 rules apply: Inspect, check, or test the meter within 7 working days in Urban areas and within 15 working days in Rural areas of receiving a complainta defective meter is generally replaced within 15 days after inspection/testing. After 6th Dec 2023, amendment rules apply: If found defective, replace the meter and restore the electricity supply within 24 hours in Urban areas and within 72 hours in Rural areas from the time of inspection or testing. | N/A | N/A | Single phase: 10,113 / Three phase: 3,504 | No. of faulty meters pending at year-end | No | N/A | No benchmark defined in regulations.
2023-24 | New connections | Release of new connections | Releasing and energising a new electricity connection upon receiving the applicant's full payment of the demand note and necessary test report. | Before 6th Dec 2023: General-purpose demand note within 7 days and connection within 20 days after payment/formalities where the distribution system exists; where mains/substation extension is needed, the outer period is 2 months Urban / 4 months Rural. After 6th Dec 2023: Energise and release the connection within: 7 days in Urban areas and 10 days in Rural areas if provided from the existing distribution network; 15 days if network modification requires extending the LT line up to 150 metres; 21 days if network modification requires extending the LT line more than 150 metres and/or augmenting the distribution transformer; 30 days if network modification requires erecting a new distribution transformer; 90 days if network modification requires erecting a new HT line and distribution transformer and/or augmenting the existing HT line network; 180 days if network modification requires erecting/augmenting an EHT level line and/or substation. | N/A | N/A | 94.25 | % of connections released out of the total applications | No | N/A | No benchmark defined in regulations.
2024-25 | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Quality of Supply | Neutral Voltage | The presence of electrical potential on the neutral conductor relative to earth, indicating an imbalance or faulty grounding. | If rectification is not feasible immediately, inform the consumer of the likely completion timeline within 3 days in Urban areas and 7 days in Rural areas. | 2 | Keep neutral voltage from exceeding 2% of the supply voltage. | N/A | N/A |  |  | Reported data reads up to <45,000 pages.
2024-25 | Cosumer complaints | Classification of Complaints | Organizing consumer complaints into specific technical, billing, or service categories. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data reads up to <45,000 pages.
2024-25 | Restoration of Supply | Faulty meter | Meter reported by a consumer or detected by the utility as defective, stopped, burnt, stolen, or improperly recording. | Inspect, check, or test the meter within 7 working days in Urban areas and within 15 working days in Rural areas of receiving a complaint. If found defective, replace the meter and restore the electricity supply within 24 hours in Urban areas and within 72 hours in Rural areas from the time of inspection or testing. | N/A | N/A | Single-Phase: 9,340/ Three-Phase: 2,588 | No. of faulty meters pending at year-end | No | N/A | Reported data reads up to <45,000 pages.
2024-25 | New connections | Release of new connections | Releasing and energising a new electricity connection upon receiving the applicant's full payment of the demand note and necessary test report. | Energise and release the connection within: 7 days in Urban areas and 10 days in Rural areas if provided from the existing distribution network; 15 days if network modification requires extending the LT line up to 150 metres; 21 days if network modification requires extending the LT line more than 150 metres and/or augmenting the distribution transformer; 30 days if network modification requires erecting a new distribution transformer; 90 days if network modification requires erecting a new HT line and distribution transformer and/or augmenting the existing HT line network; 180 days if network modification requires erecting/augmenting an EHT level line and/or substation. | N/A | N/A | N/A | N/A | No | N/A | new-connection release-status table not found in the available source
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Quality of Supply | Neutral Voltage | The presence of electrical potential on the neutral conductor relative to earth, indicating an imbalance or faulty grounding. | If rectification is not feasible immediately, inform the consumer of the likely completion timeline within 3 days in Urban areas and 7 days in Rural areas. | 2 | Keep neutral voltage from exceeding 2% of the supply voltage. | 0 | No. of deviation of results from the sample test
2025-26 | Cosumer complaints | Classification of Complaints | Organizing consumer complaints into specific technical, billing, or service categories. | N/A | N/A | N/A | 99.99 | % of registered complaints redressed in standard time | No | N/A | No benchmark defined in regulations.
2025-26 | Restoration of Supply | Faulty meter | Meter reported by a consumer or detected by the utility as defective, stopped, burnt, stolen, or improperly recording. | Inspect, check, or test the meter within 7 working days in Urban areas and within 15 working days in Rural areas of receiving a complaint. If found defective, replace the meter and restore the electricity supply within 24 hours in Urban areas and within 72 hours in Rural areas from the time of inspection or testing. | N/A | N/A | Single phase: 11,156 /Three phase: 4,719 | No. of faulty meters pending at year-end | No | N/A | No benchmark defined in regulations.
2025-26 | New connections | Release of new connections | Releasing and energising a new electricity connection upon receiving the applicant's full payment of the demand note and necessary test report. | Energise and release the connection within: 7 days in Urban areas and 10 days in Rural areas if provided from the existing distribution network; 15 days if network modification requires extending the LT line up to 150 metres; 21 days if network modification requires extending the LT line more than 150 metres and/or augmenting the distribution transformer; 30 days if network modification requires erecting a new distribution transformer; 90 days if network modification requires erecting a new HT line and distribution transformer and/or augmenting the existing HT line network; 180 days if network modification requires erecting/augmenting an EHT level line and/or substation. | N/A | N/A | N/A | % of connections released out of the total applications | No | N/A | Data not reported

## PGVCL, GUJARAT
Paschim Gujarat Vij Company Limited
Gujarat Electricity Regulatory Commission (Standards of Performance of Distribution Licensees) Regulations, 2023. | Gujarat Electricity Regulatory Commission (Standard of Performance of Distribution Licensee) Regulations, 2005 | 2005 Regulations apply up to 5 Dec 2023 and the 2023 Regulations apply from 6 Dec 2023. FY 2023-24 must be treated as a split-regulation year.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Quality of Supply | Neutral Voltage | The presence of electrical potential on the neutral conductor relative to earth, indicating an imbalance or faulty grounding. | If rectification is not feasible immediately, inform the consumer of the likely completion timeline within 3 days in Urban areas and 7 days in Rural areas. | 2 | Keep neutral voltage from exceeding 2% of the supply voltage. | 0 | No. of deviation of results from the sample test
2021-22 | Cosumer complaints | Classification of Complaints | Organizing consumer complaints into specific technical, billing, or service categories. | N/A | N/A | N/A | 99.11 | % of registered complaints redressed in standard time | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Faulty meter | Meter reported by a consumer or detected by the utility as defective, stopped, burnt, stolen, or improperly recording. | inspect/test within 7 working days Urban / 15 working days Rural; a defective meter is generally replaced within 15 days after inspection/testing. | N/A | N/A | Total : 52,428; Single-Phase : 23,657; Three-Phase: 28,771 | No. of faulty meters pending at year-end | No | N/A | No benchmark defined in regulations.
2021-22 | New connections | Release of new connections | Releasing and energising a new electricity connection upon receiving the applicant's full payment of the demand note and necessary test report. | Energise and release the connection within: 7 days in Urban areas and 10 days in Rural areas if provided from the existing distribution network; 15 days if network modification requires extending the LT line up to 150 metres; 21 days if network modification requires extending the LT line more than 150 metres and/or augmenting the distribution transformer; 30 days if network modification requires erecting a new distribution transformer; 90 days if network modification requires erecting a new HT line and distribution transformer and/or augmenting the existing HT line network; 180 days if network modification requires erecting/augmenting an EHT level line and/or substation. | N/A | N/A | 69.75 | % of connections released out of the total applications | No | N/A | Data not reported
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Quality of Supply | Neutral Voltage | The presence of electrical potential on the neutral conductor relative to earth, indicating an imbalance or faulty grounding. | If rectification is not feasible immediately, inform the consumer of the likely completion timeline within 3 days in Urban areas and 7 days in Rural areas. | 2 | Keep neutral voltage from exceeding 2% of the supply voltage. | 0 | No. of deviation of results from the sample test
2022-23 | Cosumer complaints | Classification of Complaints | Organizing consumer complaints into specific technical, billing, or service categories. | N/A | N/A | N/A | N/A | % of registered complaints redressed in standard time | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Faulty meter | Meter reported by a consumer or detected by the utility as defective, stopped, burnt, stolen, or improperly recording. | inspect/test within 7 working days Urban / 15 working days Rural; a defective meter is generally replaced within 15 days after inspection/testing. | N/A | N/A | Total : 52,647; Single-Phase : 19,171; Three-Phase: 33,476 | No. of faulty meters pending at year-end | No | N/A | No benchmark defined in regulations.
2022-23 | New connections | Release of new connections | Releasing and energising a new electricity connection upon receiving the applicant's full payment of the demand note and necessary test report. | Energise and release the connection within: 7 days in Urban areas and 10 days in Rural areas if provided from the existing distribution network; 15 days if network modification requires extending the LT line up to 150 metres; 21 days if network modification requires extending the LT line more than 150 metres and/or augmenting the distribution transformer; 30 days if network modification requires erecting a new distribution transformer; 90 days if network modification requires erecting a new HT line and distribution transformer and/or augmenting the existing HT line network; 180 days if network modification requires erecting/augmenting an EHT level line and/or substation. | N/A | N/A | 83.91 | % of connections released out of the total applications | No | N/A | Data not reported
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Quality of Supply | Neutral Voltage | The presence of electrical potential on the neutral conductor relative to earth, indicating an imbalance or faulty grounding. | If rectification is not feasible immediately, inform the consumer of the likely completion timeline within 3 days in Urban areas and 7 days in Rural areas. | 2 | Keep neutral voltage from exceeding 2% of the supply voltage. | 0 | No. of deviation of results from the sample test
2023-24 | Cosumer complaints | Classification of Complaints | Organizing consumer complaints into specific technical, billing, or service categories. | N/A | N/A | N/A | 99.35 | % of registered complaints redressed in standard time | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Faulty meter | Meter reported by a consumer or detected by the utility as defective, stopped, burnt, stolen, or improperly recording. | Before 6 Dec 2023, the 2005 rules apply: Inspect, check, or test the meter within 7 working days in Urban areas and within 15 working days in Rural areas of receiving a complainta defective meter is generally replaced within 15 days after inspection/testing. After 6th Dec 2023, amendment rules apply: If found defective, replace the meter and restore the electricity supply within 24 hours in Urban areas and within 72 hours in Rural areas from the time of inspection or testing. | N/A | N/A | Total : 71,122; Single-Phase : 29,599; Three-Phase: 41,523 | No. of faulty meters pending at year-end | No | N/A | No benchmark defined in regulations.
2023-24 | New connections | Release of new connections | Releasing and energising a new electricity connection upon receiving the applicant's full payment of the demand note and necessary test report. | Before 6th Dec 2023: General-purpose demand note within 7 days and connection within 20 days after payment/formalities where the distribution system exists; where mains/substation extension is needed, the outer period is 2 months Urban / 4 months Rural. After 6th Dec 2023: Energise and release the connection within: 7 days in Urban areas and 10 days in Rural areas if provided from the existing distribution network; 15 days if network modification requires extending the LT line up to 150 metres; 21 days if network modification requires extending the LT line more than 150 metres and/or augmenting the distribution transformer; 30 days if network modification requires erecting a new distribution transformer; 90 days if network modification requires erecting a new HT line and distribution transformer and/or augmenting the existing HT line network; 180 days if network modification requires erecting/augmenting an EHT level line and/or substation. | N/A | N/A | 88.03 | % of connections released out of the total applications | No | N/A | Data not reported
2024-25 | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Quality of Supply | Neutral Voltage | The presence of electrical potential on the neutral conductor relative to earth, indicating an imbalance or faulty grounding. | If rectification is not feasible immediately, inform the consumer of the likely completion timeline within 3 days in Urban areas and 7 days in Rural areas. | 2 | Keep neutral voltage from exceeding 2% of the supply voltage. | N/A | No. of deviation of results from the sample test
2024-25 | Cosumer complaints | Classification of Complaints | Organizing consumer complaints into specific technical, billing, or service categories. | N/A | N/A | N/A | N/A | % of registered complaints redressed in standard time | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | Faulty meter | Meter reported by a consumer or detected by the utility as defective, stopped, burnt, stolen, or improperly recording. | Inspect, check, or test the meter within 7 working days in Urban areas and within 15 working days in Rural areas of receiving a complaint. If found defective, replace the meter and restore the electricity supply within 24 hours in Urban areas and within 72 hours in Rural areas from the time of inspection or testing. | N/A | N/A | N/A | No. of faulty meters pending at year-end | No | N/A | No benchmark defined in regulations.
2024-25 | New connections | Release of new connections | Releasing and energising a new electricity connection upon receiving the applicant's full payment of the demand note and necessary test report. | Energise and release the connection within: 7 days in Urban areas and 10 days in Rural areas if provided from the existing distribution network; 15 days if network modification requires extending the LT line up to 150 metres; 21 days if network modification requires extending the LT line more than 150 metres and/or augmenting the distribution transformer; 30 days if network modification requires erecting a new distribution transformer; 90 days if network modification requires erecting a new HT line and distribution transformer and/or augmenting the existing HT line network; 180 days if network modification requires erecting/augmenting an EHT level line and/or substation. | N/A | N/A | N/A | % of connections released out of the total applications | No | N/A | Data not reported
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Quality of Supply | Neutral Voltage | The presence of electrical potential on the neutral conductor relative to earth, indicating an imbalance or faulty grounding. | If rectification is not feasible immediately, inform the consumer of the likely completion timeline within 3 days in Urban areas and 7 days in Rural areas. | 2 | Keep neutral voltage from exceeding 2% of the supply voltage. | N/A | No. of deviation of results from the sample test
2025-26 | Cosumer complaints | Classification of Complaints | Organizing consumer complaints into specific technical, billing, or service categories. | N/A | N/A | N/A | N/A | % of registered complaints redressed in standard time | No | N/A | Data not reported
2025-26 | Restoration of Supply | Faulty meter | Meter reported by a consumer or detected by the utility as defective, stopped, burnt, stolen, or improperly recording. | Inspect, check, or test the meter within 7 working days in Urban areas and within 15 working days in Rural areas of receiving a complaint. If found defective, replace the meter and restore the electricity supply within 24 hours in Urban areas and within 72 hours in Rural areas from the time of inspection or testing. | N/A | N/A | N/A | No. of faulty meters pending at year-end | No | N/A | No benchmark defined in regulations.
2025-26 | New connections | Release of new connections | Releasing and energising a new electricity connection upon receiving the applicant's full payment of the demand note and necessary test report. | Energise and release the connection within: 7 days in Urban areas and 10 days in Rural areas if provided from the existing distribution network; 15 days if network modification requires extending the LT line up to 150 metres; 21 days if network modification requires extending the LT line more than 150 metres and/or augmenting the distribution transformer; 30 days if network modification requires erecting a new distribution transformer; 90 days if network modification requires erecting a new HT line and distribution transformer and/or augmenting the existing HT line network; 180 days if network modification requires erecting/augmenting an EHT level line and/or substation. | N/A | N/A | N/A | % of connections released out of the total applications | No | N/A | Data not reported

## UGVCL, GUJARAT
Uttar Gujarat Vij Company Limited
Gujarat Electricity Regulatory Commission (Standards of Performance of Distribution Licensees) Regulations, 2023. | Gujarat Electricity Regulatory Commission (Standard of Performance of Distribution Licensee) Regulations, 2005 | 2005 Regulations apply up to 5 Dec 2023 and the 2023 Regulations apply from 6 Dec 2023. FY 2023-24 must be treated as a split-regulation year.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Quality of Supply | Neutral Voltage | The presence of electrical potential on the neutral conductor relative to earth, indicating an imbalance or faulty grounding. | If rectification is not feasible immediately, inform the consumer of the likely completion timeline within 3 days in Urban areas and 7 days in Rural areas. | 2 | Keep neutral voltage from exceeding 2% of the supply voltage. | 5,435 (or 2 category deviations) | No. of deviation of results from the sample test
2021-22 | Cosumer complaints | Classification of Complaints | Organizing consumer complaints into specific technical, billing, or service categories. | N/A | N/A | N/A | 99.9917% of registered complaints redressed in standard time | % of registered complaints redressed in standard time | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Faulty meter | Meter reported by a consumer or detected by the utility as defective, stopped, burnt, stolen, or improperly recording. | Inspect, check, or test the meter within 7 working days in Urban areas and within 15 working days in Rural areas of receiving a complaint. If found defective, replace the meter and restore the electricity supply within 24 hours in Urban areas and within 72 hours in Rural areas from the time of inspection or testing. | N/A | N/A | 614 | Total no. of faulty meters pending at year-end | No | N/A | No benchmark defined in regulations.
2021-22 | New connections | Release of new connections | Releasing and energising a new electricity connection upon receiving the applicant's full payment of the demand note and necessary test report. | Energise and release the connection within: 7 days in Urban areas and 10 days in Rural areas if provided from the existing distribution network; 15 days if network modification requires extending the LT line up to 150 metres; 21 days if network modification requires extending the LT line more than 150 metres and/or augmenting the distribution transformer; 30 days if network modification requires erecting a new distribution transformer; 90 days if network modification requires erecting a new HT line and distribution transformer and/or augmenting the existing HT line network; 180 days if network modification requires erecting/augmenting an EHT level line and/or substation. | N/A | N/A | 73.99 | % of connections released out of the total applications | No | N/A | Data not reported
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Quality of Supply | Neutral Voltage | The presence of electrical potential on the neutral conductor relative to earth, indicating an imbalance or faulty grounding. | If rectification is not feasible immediately, inform the consumer of the likely completion timeline within 3 days in Urban areas and 7 days in Rural areas. | 2 | Keep neutral voltage from exceeding 2% of the supply voltage. | 2 | No. of deviation of results from the sample test
2022-23 | Cosumer complaints | Classification of Complaints | Organizing consumer complaints into specific technical, billing, or service categories. | N/A | N/A | N/A | 100 | % of registered complaints redressed in standard time | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Faulty meter | Meter reported by a consumer or detected by the utility as defective, stopped, burnt, stolen, or improperly recording. | inspect/test within 7 working days Urban / 15 working days Rural; a defective meter is generally replaced within 15 days after inspection/testing. | N/A | N/A | 1271 | Total no. of faulty meters pending at year-end | No | N/A | No benchmark defined in regulations.
2022-23 | New connections | Release of new connections | Releasing and energising a new electricity connection upon receiving the applicant's full payment of the demand note and necessary test report. | Energise and release the connection within: 7 days in Urban areas and 10 days in Rural areas if provided from the existing distribution network; 15 days if network modification requires extending the LT line up to 150 metres; 21 days if network modification requires extending the LT line more than 150 metres and/or augmenting the distribution transformer; 30 days if network modification requires erecting a new distribution transformer; 90 days if network modification requires erecting a new HT line and distribution transformer and/or augmenting the existing HT line network; 180 days if network modification requires erecting/augmenting an EHT level line and/or substation. | N/A | N/A | 80.56 | % of connections released out of the total applications | No | N/A | Data not reported
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Quality of Supply | Neutral Voltage | The presence of electrical potential on the neutral conductor relative to earth, indicating an imbalance or faulty grounding. | If rectification is not feasible immediately, inform the consumer of the likely completion timeline within 3 days in Urban areas and 7 days in Rural areas. | 2 | Keep neutral voltage from exceeding 2% of the supply voltage. | 2 | No. of deviation of results from the sample test
2023-24 | Cosumer complaints | Classification of Complaints | Organizing consumer complaints into specific technical, billing, or service categories. | N/A | N/A | N/A | 99.99 | % of registered complaints redressed in standard time | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Faulty meter | Meter reported by a consumer or detected by the utility as defective, stopped, burnt, stolen, or improperly recording. | Before 6 Dec 2023, the 2005 rules apply: Inspect, check, or test the meter within 7 working days in Urban areas and within 15 working days in Rural areas of receiving a complainta defective meter is generally replaced within 15 days after inspection/testing. After 6th Dec 2023, amendment rules apply: If found defective, replace the meter and restore the electricity supply within 24 hours in Urban areas and within 72 hours in Rural areas from the time of inspection or testing. | N/A | N/A | 14952 | Total no. of faulty meters pending at year-end | No | N/A | No benchmark defined in regulations.
2023-24 | New connections | Release of new connections | Releasing and energising a new electricity connection upon receiving the applicant's full payment of the demand note and necessary test report. | Before 6th Dec 2023: General-purpose demand note within 7 days and connection within 20 days after payment/formalities where the distribution system exists; where mains/substation extension is needed, the outer period is 2 months Urban / 4 months Rural. After 6th Dec 2023: Energise and release the connection within: 7 days in Urban areas and 10 days in Rural areas if provided from the existing distribution network; 15 days if network modification requires extending the LT line up to 150 metres; 21 days if network modification requires extending the LT line more than 150 metres and/or augmenting the distribution transformer; 30 days if network modification requires erecting a new distribution transformer; 90 days if network modification requires erecting a new HT line and distribution transformer and/or augmenting the existing HT line network; 180 days if network modification requires erecting/augmenting an EHT level line and/or substation. | N/A | N/A | 71.36 | % of connections released out of the total applications | No | N/A | Data not reported
2024-25 | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Quality of Supply | Neutral Voltage | The presence of electrical potential on the neutral conductor relative to earth, indicating an imbalance or faulty grounding. | If rectification is not feasible immediately, inform the consumer of the likely completion timeline within 3 days in Urban areas and 7 days in Rural areas. | 2 | Keep neutral voltage from exceeding 2% of the supply voltage. | 1 | No. of deviation of results from the sample test
2024-25 | Cosumer complaints | Classification of Complaints | Organizing consumer complaints into specific technical, billing, or service categories. | N/A | N/A | N/A | 93.8 | % of registered complaints redressed in standard time | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | Faulty meter | Meter reported by a consumer or detected by the utility as defective, stopped, burnt, stolen, or improperly recording. | inspect/test within 7 working days Urban / 15 working days Rural; a defective meter is generally replaced within 15 days after inspection/testing. | N/A | N/A | 8510 | Total no. of faulty meters pending at year-end | No | N/A | No benchmark defined in regulations.
2024-25 | New connections | Release of new connections | Releasing and energising a new electricity connection upon receiving the applicant's full payment of the demand note and necessary test report. | Energise and release the connection within: 7 days in Urban areas and 10 days in Rural areas if provided from the existing distribution network; 15 days if network modification requires extending the LT line up to 150 metres; 21 days if network modification requires extending the LT line more than 150 metres and/or augmenting the distribution transformer; 30 days if network modification requires erecting a new distribution transformer; 90 days if network modification requires erecting a new HT line and distribution transformer and/or augmenting the existing HT line network; 180 days if network modification requires erecting/augmenting an EHT level line and/or substation. | N/A | N/A | N/A | % of connections released out of the total applications | No | N/A | Data not reported
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Quality of Supply | Neutral Voltage | The presence of electrical potential on the neutral conductor relative to earth, indicating an imbalance or faulty grounding. | If rectification is not feasible immediately, inform the consumer of the likely completion timeline within 3 days in Urban areas and 7 days in Rural areas. | 2 | Keep neutral voltage from exceeding 2% of the supply voltage. | 1 | No. of deviation of results from the sample test
2025-26 | Cosumer complaints | Classification of Complaints | Organizing consumer complaints into specific technical, billing, or service categories. | N/A | N/A | N/A | 95.7 | % of registered complaints redressed in standard time | No | N/A | No benchmark defined in regulations.
2025-26 | Restoration of Supply | Faulty meter | Meter reported by a consumer or detected by the utility as defective, stopped, burnt, stolen, or improperly recording. | Inspect, check, or test the meter within 7 working days in Urban areas and within 15 working days in Rural areas of receiving a complaint. If found defective, replace the meter and restore the electricity supply within 24 hours in Urban areas and within 72 hours in Rural areas from the time of inspection or testing. | N/A | N/A | 13063 | Total no. of faulty meters pending at year-end | No | N/A | No benchmark defined in regulations.
2025-26 | New connections | Release of new connections | Releasing and energising a new electricity connection upon receiving the applicant's full payment of the demand note and necessary test report. | Energise and release the connection within: 7 days in Urban areas and 10 days in Rural areas if provided from the existing distribution network; 15 days if network modification requires extending the LT line up to 150 metres; 21 days if network modification requires extending the LT line more than 150 metres and/or augmenting the distribution transformer; 30 days if network modification requires erecting a new distribution transformer; 90 days if network modification requires erecting a new HT line and distribution transformer and/or augmenting the existing HT line network; 180 days if network modification requires erecting/augmenting an EHT level line and/or substation. | N/A | N/A | N/A | % of connections released out of the total applications | No | N/A | Data not reported